## Squarefoot_Estimate
|  | Square Foot Cost Estimate Report |  |  | Date: | 11/12/2022
Estimate Name: |  | office
Building Type: |  | Hospital, 4-8 Story with Curtain Wall / Rigid Steel
Location: |  | NATIONAL AVERAGE
Story Count: |  | 8
Story Height (L.F.): |  | 10
Floor Area (S.F.): |  | 280000
Labor Type: |  | OPN
Basement Included: |  | No | [5 empty] | Assembly Customization Type:
Data Release: |  | Year 2022 | Costs are derived from a building model with basic components. | [5 empty] | Added
Cost Per Square Foot: |  | $275.75 | Scope differences and market conditions can cause costs to vary significantly. | [5 empty] | Partially Swapped
Building Cost: |  | $77,211,251.02 | [6 empty] | Fully Swapped
|  |  | Quantity | % of Total | Cost Per S.F. | Cost
A |  | Substructure |  | 1.13 | 2.28 | 639574.25 | 1
A1010 |  | Standard Foundations |  |  | 0.38 | 106524.25 | 3
A10101051560 |  | Foundation wall, CIP, 4' wall height, direct chute, .148 CY/LF, 7.2 PLF, 12" thick | 378 |  | 0.12 | 32508 | 4
A10101103100 |  | Strip footing, concrete, reinforced, load 14.8 KLF, soil bearing capacity 6 KSF, 12" deep x 32" wide | 472.5 |  | 0.09 | 24806.25 | 4
A10102107700 |  | Spread footings, 3000 PSI concrete, load 200K, soil bearing capacity 6 KSF, 6' - 0" square x 20" deep | 51.8 |  | 0.18 | 49210 | 4
A1030 |  | Slab on Grade |  |  | 1.88 | 526750 | 3
A10301204560 |  | Slab on grade, 6" thick, heavy industrial, reinforced | 35000 |  | 1.88 | 526750 | 4
A2010 |  | Basement Excavation |  |  | 0.02 | 6300 | 3
A20101105740 |  | Excavate and fill, 30,000 SF, 4' deep, sand, gravel, or common earth, on site storage | 35000 |  | 0.02 | 6300 | 4
B |  | Shell |  | 11.71 | 23.69 | 6633816.392 | 1
B1010 |  | Floor Construction |  |  | 14.87 | 4164888.532 | 3
B10102482440 |  | Floor, concrete, slab form, steel joists, joist girder, 1.5" 22 ga metal deck, on columns, 50'x50' bay, 32" deep, 40 PSF superimposed load, 84 PSF total load | 245000 |  | 13.47 | 3770550 | 4
B10102482450 |  | Floor, concrete, slab form, steel joists, joist girder, 1.5" 22 ga metal deck, on columns, 50'x50'' bay, 40 PSF superimposed load, 84 PSF total load, for columns add | 245000 |  | 1.12 | 313600 | 4
B10107203650 |  | Fireproofing, gypsum board, fire rated, 2 layer, 1" thick, 10" steel column, 3 hour rating, 17 PLF | 2199.96 |  | 0.29 | 80738.532 | 4
B1020 |  | Roof Construction |  |  | 1.66 | 464800 | 3
B10201245800 |  | Roof, steel joists, joist girder, 1.5" 22 ga metal deck, on columns, 50'x50' bay, 40 PSF superimposed load, 59" deep, 64 PSF total load | 35000 |  | 1.5 | 420000 | 4
B10201245850 |  | Roof, steel joists, joist girder, 1.5" 22 ga metal deck, on columns, 50'x50' bay, 40 PSF superimposed load, 59" deep, 64 PSF total load, add for columns | 35000 |  | 0.16 | 44800 | 4
B2020 |  | Exterior Windows |  |  | 5.25 | 1469936.16 | 3
B20202102000 |  | Aluminum flush tube frame, thermo-break frame, 2.25" x 4.5", 5'x6' opening, no intermediate horizontals | 29937.6 |  | 3.14 | 878668.56 | 4
B20202202000 |  | Glazing panel, plate glass, 1/4" thick, clear | 29937.6 |  | 2.11 | 591267.6 | 4
B2030 |  | Exterior Doors |  |  | 1.08 | 301413 | 3
B20301107150 |  | Door, aluminum & glass, with transom, full vision, double door, hardware, 6'-0" x 10'-0" opening | 4.2 |  | 0.13 | 37275 | 4
B20301107250 |  | Door, aluminum & glass, with transom, non-standard, double door, hardware, 6'-0" x 10'-0" opening | 26.6 |  | 0.84 | 235410 | 4
B20302203450 |  | Door, steel 18 gauge, hollow metal, 1 door with frame, no label, 3'-0" x 7'-0" opening | 8.4 |  | 0.1 | 28728 | 4
B3010 |  | Roof Coverings |  |  | 0.79 | 221421.9 | 3
B30101203400 |  | Roofing, single ply membrane, EPDM, 60 mils, loosely laid, stone ballast | 35000 |  | 0.22 | 61950 | 4
B30103202700 |  | Insulation, rigid, roof deck, extruded polystyrene, 40 PSI compressive strength, 4" thick, R20 | 35000 |  | 0.52 | 144900 | 4
B30104201400 |  | Roof edges, aluminum, duranodic, .050" thick, 6" face | 378 |  | 0.04 | 11245.5 | 4
B30106305100 |  | Gravel stop, aluminum, extruded, 4", mill finish, .050" thick | 378 |  | 0.01 | 3326.4 | 4
B3020 |  | Roof Openings |  |  | 0.04 | 11356.8 | 3
B30202100300 |  | Roof hatch, with curb, 1" fiberglass insulation, 2'-6" x 3'-0", galvanized steel, 165 lbs | 8.4 |  | 0.04 | 11356.8 | 4
C |  | Interiors |  | 20.74 | 41.97 | 11752567.065 | 1
C1010 |  | Partitions |  |  | 6.83 | 1913644.4444 | 3
C10101045500 |  | Concrete block (CMU) partition, light weight, hollow, 6" thick, no finish | 31111.11 |  | 0.91 | 253866.6667 | 4
C10101265425 |  | Metal partition, 5/8"fire rated gypsum board face, no base,3 -5/8" @ 24" OC framing, same opposite face, sound attenuation insulation | 280000 |  | 5.54 | 1551200 | 4
C10101280850 |  | Gypsum board, 1 face only, 5/8" with 1/16" lead | 6222.22 |  | 0.39 | 108577.7778 | 4
C1020 |  | Interior Doors |  |  | 11.11 | 3110281.4815 | 3
C10201022600 |  | Door, single leaf, kd steel frame, hollow metal, commercial quality, flush, 3'-0" x 7'-0" x 1-3/8" | 1659.26 |  | 8.34 | 2336237.037 | 4
C10201022700 |  | Door, single leaf, kd steel frame, metal fire, commercial quality, 3'-0" x 7'-0" x 1-3/8" | 414.81 |  | 2.76 | 774044.4444 | 4
C1030 |  | Fittings |  |  | 0.42 | 117530.028 | 3
C10307300100 |  | Partitions, hospital curtain, ceiling hung, poly oxford cloth | 3492.72 |  | 0.42 | 117530.028 | 4
C2010 |  | Stair Construction |  |  | 1.51 | 422240 | 3
C20101100720 |  | Stairs, steel, pan tread for conc in-fill, picket rail,12 risers w/ landing | 36.4 |  | 1.51 | 422240 | 4
C3010 |  | Wall Finishes |  |  | 5.6 | 1567191.1111 | 3
C30102300140 |  | Painting, interior on plaster and drywall, walls & ceilings, roller work, primer & 2 coats | 336000 |  | 0.88 | 245280 | 4
C30102301940 |  | Ceramic tile, thin set, 4-1/4" x 4-1/4" | 217777.78 |  | 4.72 | 1321911.1111 | 4
C3020 |  | Floor Finishes |  |  | 7.54 | 2110080 | 3
C30204100360 |  | Composition flooring, epoxy terrazzo, recycled porcelain | 28000 |  | 1.97 | 551600 | 4
C30204101120 |  | Terrazzo, maximum | 28000 |  | 2.76 | 772800 | 4
C30204101600 |  | Vinyl, composition tile, maximum | 168000 |  | 1.31 | 367920 | 4
C30204101720 |  | Tile, ceramic natural clay | 56000 |  | 1.49 | 417760 | 4
C3030 |  | Ceiling Finishes |  |  | 8.97 | 2511600 | 3
C30302106000 |  | Acoustic ceilings, 3/4" fiberglass board, 24" x 48" tile, tee grid, suspended support | 280000 |  | 8.97 | 2511600 | 4
D |  | Services |  | 52.8 | 106.86 | 29920719.18 | 1
D1010 |  | Elevators and Lifts |  |  | 7.18 | 2011800 | 3
D10101109250 |  | Traction, geared hospital, 6000 lb, 6 floors, 12' story height, 2 car group, 200 FPM | 8.4 |  | 7.18 | 2011800 | 4
D2010 |  | Plumbing Fixtures |  |  | 8.55 | 2394875 | 3
D20101102080 |  | Water closet, vitreous china, bowl only with flush valve, wall hung | 214.2 |  | 2.93 | 821457 | 4
D20102102000 |  | Urinal, vitreous china, wall hung | 71.4 |  | 0.35 | 96747 | 4
D20103102080 |  | Lavatory w/trim, wall hung, PE on CI, 19" x 17" | 214.2 |  | 1.62 | 454104 | 4
D20104102280 |  | Kitchen sink w/trim, raised deck, PE on CI, 42" x 21" dual level, triple bowl | 8.4 |  | 0.08 | 23310 | 4
D20104201840 |  | Laundry sink w/trim, PE on CI, black iron frame, 48" x 21" double compartment | 16.8 |  | 0.14 | 37968 | 4
D20104404300 |  | Service sink w/trim, PE on CI,wall hung w/rim guard, 22" x 18" | 16.8 |  | 0.31 | 87360 | 4
D20105102120 |  | Bathtub, recessed, PE on CI, mat bottom, 5'-6" long | 116.2 |  | 1.57 | 439236 | 4
D20107101680 |  | Shower, stall, baked enamel, terrazzo receptor, 36" square | 116.2 |  | 1.4 | 391013 | 4
D20108201920 |  | Water cooler, electric, wall hung, wheelchair type, 7.5 GPH | 18.2 |  | 0.16 | 43680 | 4
D2020 |  | Domestic Water Distribution |  |  | 10.64 | 2977915.5 | 3
D20202402420 |  | Electric water heater, commercial, 100 < F rise, 1000 gal, 480 KW 1970 GPH | 21.42 |  | 10.64 | 2977915.5 | 4
D2040 |  | Rain Water Drainage |  |  | 0.61 | 170940 | 3
D20402104280 |  | Roof drain, CI, soil,single hub, 5" diam, 10' high | 28 |  | 0.27 | 75460 | 4
D20402104320 |  | Roof drain, CI, soil,single hub, 5" diam, for each additional foot add | 1736 |  | 0.34 | 95480 | 4
D3010 |  | Energy Supply |  |  | 5.34 | 1495200 | 3
D30105600110 |  | Hot water reheat system for 200,000 SF hospital | 280000 |  | 5.34 | 1495200 | 4
D3020 |  | Heat Generating Systems |  |  | 0.53 | 148662.5 | 3
D30201060900 |  | Boiler, electric, steel, steam, 510 KW, 1,740 MBH | 3.5 |  | 0.53 | 148662.5 | 4
D3030 |  | Cooling Generating Systems |  |  | 3.37 | 943040 | 3
D30301301020 |  | Chiller, reciprocating, water cooled, standard controls, 100 ton | 1.4 |  | 0.5 | 139720 | 4
D30301301030 |  | Chiller, reciprocating, water cooled, standard controls, 150 ton | 2.8 |  | 1.26 | 352800 | 4
D30301301040 |  | Chiller, reciprocating, water cooled, standard controls, 200 ton | 2.8 |  | 1.61 | 450520 | 4
D3090 |  | Other HVAC Systems/Equip |  |  | 40.91 | 11453610 | 3
D30905100210 |  | Ductwork for 200,000 SF hospital model | 448000 |  | 22.08 | 6182400 | 4
D30905101020 |  | Boiler, cast iron, gas, hot water, 2856 MBH | 5.6 |  | 1.69 | 473200 | 4
D30905101030 |  | Boiler, cast iron, gas, hot water, 320 MBH | 5.6 |  | 0.34 | 94220 | 4
D30905102010 |  | AHU, rooftop, cool/heat coils, VAV, filters, 5,000 CFM | 2.8 |  | 0.52 | 146160 | 4
D30905102020 |  | AHU, rooftop, cool/heat coils, VAV, filters, 10,000 CFM | 2.8 |  | 0.98 | 275240 | 4
D30905102030 |  | AHU, rooftop, cool/heat coils, VAV, filters, 20,000 CFM | 5.6 |  | 3.64 | 1019200 | 4
D30905102040 |  | VAV terminal, cooling, hot water reheat, with actuator / controls, 200 CFM | 280 |  | 5.82 | 1631000 | 4
D30905102045 |  | AHU, rooftop, cool/heat coils, VAV, filters, 30,000 CFM | 5.6 |  | 4.23 | 1184400 | 4
D30905102060 |  | Roof vent. system, power, centrifugal, aluminum, galvanized curb, back draft damper, 1500 CFM | 2.8 |  | 0.09 | 24150 | 4
D30905102070 |  | Roof vent. system, power, centrifugal, aluminum, galvanized curb, back draft damper, 2750 CFM | 5.6 |  | 0.32 | 90160 | 4
D30905102080 |  | Roof vent. system, power, centrifugal, aluminum, galvanized curb, back draft damper, 5000 CFM | 1.4 |  | 0.3 | 82880 | 4
D30905102090 |  | Plate heat exchanger, 400 GPM | 2.8 |  | 0.9 | 250600 | 4
D4010 |  | Sprinklers |  |  | 2.79 | 781686.5 | 3
D40104100620 |  | Wet pipe sprinkler systems, steel, light hazard, 1 floor, 10,000 SF | 47600 |  | 0.6 | 166600 | 4
D40104100740 |  | Wet pipe sprinkler systems, steel, light hazard, each additional floor, 10,000 SF | 232400 |  | 2.14 | 599592 | 4
D40104108940 |  | Standard High Rise Accessory Package 8 story | 1.33 |  | 0.06 | 15494.5 | 4
D4020 |  | Standpipes |  |  | 0.69 | 194336.8 | 3
D40203101540 |  | Wet standpipe risers, class III, steel, black, sch 40, 4" diam pipe, 1 floor | 3.36 |  | 0.13 | 36792 | 4
D40203101560 |  | Wet standpipe risers, class III, steel, black, sch 40, 4" diam pipe, additional floors | 17.36 |  | 0.16 | 44441.6 | 4
D40204100900 |  | Cabs, hose rack assembly, & extinguisher, 2-1/2" x 1-1/2" valve & hose, steel door & frame | 16.8 |  | 0.03 | 8803.2 | 4
D40204101650 |  | Alarm, electric pressure switch (circuit closer) | 33.6 |  | 0.02 | 5157.6 | 4
D40204103050 |  | Escutcheon plate, for angle valves, polished brass, 2-1/2" | 16.8 |  | 0 | 630 | 4
D40204103650 |  | Fire pump, electric, with controller, 5" pump, 100 HP, 1000 GPM | 1.68 |  | 0.26 | 72828 | 4
D40204103700 |  | Fire pump, electric, for jockey pump system, add | 1.68 |  | 0.03 | 8568 | 4
D40204107050 |  | Siamese, with plugs & chains, polished brass, sidewalk, 4" x 2-1/2" x 2-1/2" | 2.8 |  | 0.01 | 3388 | 4
D40204108050 |  | Valves, angle, wheel handle, 300 lb, 2-1/2" | 36.4 |  | 0.04 | 10956.4 | 4
D40204108400 |  | Cabinet assembly, includes. adapter, rack, hose, and nozzle | 1.4 |  | 0.01 | 2772 | 4
D5010 |  | Electrical Service/Distribution |  |  | 1.9 | 531650 | 3
D50101301000 |  | Underground service installation, includes excavation, backfill, and compaction, 100' length, 4' depth, 3 phase, 4 wire, 277/480 volts, 2000 A | 2 |  | 0.57 | 160400 | 4
D50102300360 |  | Feeder installation 600 V, including RGS conduit and XHHW wire, 600 A | 200 |  | 0.12 | 33900 | 4
D50102300560 |  | Feeder installation 600 V, including RGS conduit and XHHW wire, 2000 A | 400 |  | 0.77 | 214400 | 4
D50102400620 |  | Switchgear installation, incl switchboard, panels & circuit breaker, 277/480 V, 2000 A | 2 |  | 0.44 | 122950 | 4
D5020 |  | Lighting and Branch Wiring |  |  | 21.3 | 5964925.5 | 3
D50201100720 |  | Receptacles incl plate, box, conduit, wire, 20 per 1000 SF,2.4 W per SF, with transformer | 490000 |  | 9.43 | 2641100 | 4
D50201300360 |  | Wall switches, 5.0 per 1000 SF | 490000 |  | 2.22 | 622300 | 4
D50201350320 |  | Miscellaneous power, 1.2 watts | 840000 |  | 1.05 | 294000 | 4
D50201400280 |  | Central air conditioning power, 4 watts | 352800 |  | 0.83 | 232848 | 4
D50201452080 |  | Motor installation, three phase, 460 V, 15 HP motor size | 15 |  | 0.13 | 35850 | 4
D50201550440 |  | Motor feeder systems, three phase, feed to 200 V 5 HP, 230 V 7.5 HP, 460 V 15 HP, 575 V 20 HP | 750 |  | 0.03 | 8587.5 | 4
D50202100500 |  | Fluorescent fixtures recess mounted in ceiling, 0.8 watt per SF, 20 FC, 5 fixtures @32 watt per 1000 SF | 672000 |  | 7.61 | 2130240 | 4
D5030 |  | Communications and Security |  |  | 2.03 | 568802.5 | 3
D50309100456 |  | Communication and alarm systems, fire detection, addressable, 100 detectors, includes outlets, boxes, conduit and wire | 7 |  | 1.93 | 540400 | 4
D50309100462 |  | Fire alarm command center, addressable with voice, excl. wire & conduit | 2.1 |  | 0.1 | 28402.5 | 4
D50309200110 |  | Internet wiring, 8 data/voice outlets per 1000 S.F. | 1 |  | 0 | 0 | 4
D5090 |  | Other Electrical Systems |  |  | 1.01 | 283274.88 | 3
D50902100680 |  | Generator sets, w/battery, charger, muffler and transfer switch, diesel engine with fuel tank, 100 kW | 1.68 |  | 0 | 665.28 | 4
D50902101000 |  | Generator sets, w/battery, charger, muffler and transfer switch, diesel engine with fuel tank, 400 kW | 1215.2 |  | 1.01 | 281926.4 | 4
D50902200300 |  | Uninterruptible power supply with standard battery pack, 15 kVA/12.75 kW | 560 |  | 0 | 683.2 | 4
E |  | Equipment & Furnishings |  | 13.63 | 27.58 | 7722131.2 | 1
E1020 |  | Institutional Equipment |  |  | 23.36 | 6539481.2 | 3
E10207100110 |  | Architectural equipment, laboratory equipment glassware washer, distilled water, economy | 4.2 |  | 0.13 | 35700 | 4
E10207100160 |  | Architectural equipment, sink, epoxy resin, 25" x 16" x 10" | 8.4 |  | 0.06 | 17052 | 4
E10207100170 |  | Architectural equipment, laboratory equipment eye wash, hand held | 8.4 |  | 0.01 | 4074 | 4
E10207105000 |  | Fume hood, complex, including fixtures and ductwork | 8.4 |  | 0.67 | 186900 | 4
E10208100730 |  | Architectural equipment, medical equipment sterilizers, floor loading, double door, 28"x67"x52" | 7 |  | 6.16 | 1725500 | 4
E10208200120 |  | Architectural equipment, medical equipment, medical gas system for large hospital | 560000 |  | 13.06 | 3656800 | 4
E10209100130 |  | Architectural equipment, kitchen equipment, commercial dish washer, semiautomatic, 50 racks/hr | 2.8 |  | 0.09 | 25186 | 4
E10209100160 |  | Architectural equipment, kitchen equipment, food warmer, counter, 1.65 KW | 8.4 |  | 0.02 | 5922 | 4
E10209100190 |  | Architectural equipment, kitchen equipment, kettles, steam jacketed, 20 gallons | 5.6 |  | 0.29 | 80718.4 | 4
E10209100200 |  | Architectural equipment, kitchen equipment, range, restaurant type, burners, 2 ovens & 24" griddle | 5.6 |  | 0.1 | 29304.8 | 4
E10209100210 |  | Architectural equipment, kitchen equipment, range hood, including CO2 system, economy | 5.6 |  | 0.05 | 14644 | 4
E10209100310 |  | Special construction, refrigerators, prefabricated, walk-in, 7'-6" high, 6' x 6' | 5600 |  | 2.71 | 757680 | 4
E1090 |  | Other Equipment |  |  | 0 | 0 | 3
E2020 |  | Moveable Furnishings |  |  | 4.22 | 1182650 | 3
E20202100250 |  | Furnishings, hospital furniture, patient wall system, no utilities, deluxe , per room | 434 |  | 4.22 | 1182650 | 4
F |  | Special Construction |  | 0 | 0 | 0 | 1
G |  | Building Sitework |  | 0 | 0 | 0 | 1
SubTotal |  |  |  | 100% | $202.39 | $56,668,808.09
Contractor Fees (General Conditions,Overhead,Profit) |  |  |  | 25.0% | $50.60 | $14,167,202.02
Architectural Fees |  |  |  | 9.0% | $22.77 | $6,375,240.91
User Fees |  |  |  | 0.0% | $0.00 | $0.00
Total Building Cost |  |  |  |  | $275.75 | $77,211,251.02
Audit Trail Notes
Date Time | Description |  |  | User Name |  | Action