## Squarefoot_Estimate
|  | Square Foot Cost Estimate Report |  |  | Date: | 11/12/2022
Estimate Name: |  | office
Building Type: |  | Hospital, 4-8 Story with Curtain Wall / Rigid Steel
Location: |  | NATIONAL AVERAGE
Story Count: |  | 6
Story Height (L.F.): |  | 10
Floor Area (S.F.): |  | 150000
Labor Type: |  | OPN
Basement Included: |  | No | [5 empty] | Assembly Customization Type:
Data Release: |  | Year 2022 | Costs are derived from a building model with basic components. | [5 empty] | Added
Cost Per Square Foot: |  | $281.28 | Scope differences and market conditions can cause costs to vary significantly. | [5 empty] | Partially Swapped
Building Cost: |  | $42,191,856.80 | [6 empty] | Fully Swapped
|  |  | Quantity | % of Total | Cost Per S.F. | Cost
A |  | Substructure |  | 1.47 | 3.04 | 455632.5 | 1
A1010 |  | Standard Foundations |  |  | 0.5 | 74882.5 | 3
A10101051560 |  | Foundation wall, CIP, 4' wall height, direct chute, .148 CY/LF, 7.2 PLF, 12" thick | 320 |  | 0.18 | 27520 | 4
A10101103100 |  | Strip footing, concrete, reinforced, load 14.8 KLF, soil bearing capacity 6 KSF, 12" deep x 32" wide | 400 |  | 0.14 | 21000 | 4
A10102107700 |  | Spread footings, 3000 PSI concrete, load 200K, soil bearing capacity 6 KSF, 6' - 0" square x 20" deep | 27.75 |  | 0.18 | 26362.5 | 4
A1030 |  | Slab on Grade |  |  | 2.51 | 376250 | 3
A10301204560 |  | Slab on grade, 6" thick, heavy industrial, reinforced | 25000 |  | 2.51 | 376250 | 4
A2010 |  | Basement Excavation |  |  | 0.03 | 4500 | 3
A20101105740 |  | Excavate and fill, 30,000 SF, 4' deep, sand, gravel, or common earth, on site storage | 25000 |  | 0.03 | 4500 | 4
B |  | Shell |  | 12.09 | 24.97 | 3745034.13 | 1
B1010 |  | Floor Construction |  |  | 14.35 | 2152100.08 | 3
B10102482440 |  | Floor, concrete, slab form, steel joists, joist girder, 1.5" 22 ga metal deck, on columns, 50'x50' bay, 32" deep, 40 PSF superimposed load, 84 PSF total load | 125000 |  | 12.82 | 1923750 | 4
B10102482450 |  | Floor, concrete, slab form, steel joists, joist girder, 1.5" 22 ga metal deck, on columns, 50'x50'' bay, 40 PSF superimposed load, 84 PSF total load, for columns add | 125000 |  | 1.07 | 160000 | 4
B10107203650 |  | Fireproofing, gypsum board, fire rated, 2 layer, 1" thick, 10" steel column, 3 hour rating, 17 PLF | 1862.4 |  | 0.46 | 68350.08 | 4
B1020 |  | Roof Construction |  |  | 2.21 | 332000 | 3
B10201245800 |  | Roof, steel joists, joist girder, 1.5" 22 ga metal deck, on columns, 50'x50' bay, 40 PSF superimposed load, 59" deep, 64 PSF total load | 25000 |  | 2 | 300000 | 4
B10201245850 |  | Roof, steel joists, joist girder, 1.5" 22 ga metal deck, on columns, 50'x50' bay, 40 PSF superimposed load, 59" deep, 64 PSF total load, add for columns | 25000 |  | 0.21 | 32000 | 4
B2020 |  | Exterior Windows |  |  | 6.22 | 933292.8 | 3
B20202102000 |  | Aluminum flush tube frame, thermo-break frame, 2.25" x 4.5", 5'x6' opening, no intermediate horizontals | 19008 |  | 3.72 | 557884.8 | 4
B20202202000 |  | Glazing panel, plate glass, 1/4" thick, clear | 19008 |  | 2.5 | 375408 | 4
B2030 |  | Exterior Doors |  |  | 1.08 | 161471.25 | 3
B20301107150 |  | Door, aluminum & glass, with transom, full vision, double door, hardware, 6'-0" x 10'-0" opening | 2.25 |  | 0.13 | 19968.75 | 4
B20301107250 |  | Door, aluminum & glass, with transom, non-standard, double door, hardware, 6'-0" x 10'-0" opening | 14.25 |  | 0.84 | 126112.5 | 4
B20302203450 |  | Door, steel 18 gauge, hollow metal, 1 door with frame, no label, 3'-0" x 7'-0" opening | 4.5 |  | 0.1 | 15390 | 4
B3010 |  | Roof Coverings |  |  | 1.07 | 160086 | 3
B30101203400 |  | Roofing, single ply membrane, EPDM, 60 mils, loosely laid, stone ballast | 25000 |  | 0.3 | 44250 | 4
B30103202700 |  | Insulation, rigid, roof deck, extruded polystyrene, 40 PSI compressive strength, 4" thick, R20 | 25000 |  | 0.69 | 103500 | 4
B30104201400 |  | Roof edges, aluminum, duranodic, .050" thick, 6" face | 320 |  | 0.06 | 9520 | 4
B30106305100 |  | Gravel stop, aluminum, extruded, 4", mill finish, .050" thick | 320 |  | 0.02 | 2816 | 4
B3020 |  | Roof Openings |  |  | 0.04 | 6084 | 3
B30202100300 |  | Roof hatch, with curb, 1" fiberglass insulation, 2'-6" x 3'-0", galvanized steel, 165 lbs | 4.5 |  | 0.04 | 6084 | 4
C |  | Interiors |  | 20.45 | 42.22 | 6332551.8756 | 1
C1010 |  | Partitions |  |  | 6.83 | 1025166.6667 | 3
C10101045500 |  | Concrete block (CMU) partition, light weight, hollow, 6" thick, no finish | 16666.67 |  | 0.91 | 136000 | 4
C10101265425 |  | Metal partition, 5/8"fire rated gypsum board face, no base,3 -5/8" @ 24" OC framing, same opposite face, sound attenuation insulation | 150000 |  | 5.54 | 831000 | 4
C10101280850 |  | Gypsum board, 1 face only, 5/8" with 1/16" lead | 3333.33 |  | 0.39 | 58166.6667 | 4
C1020 |  | Interior Doors |  |  | 11.11 | 1666222.2222 | 3
C10201022600 |  | Door, single leaf, kd steel frame, hollow metal, commercial quality, flush, 3'-0" x 7'-0" x 1-3/8" | 888.89 |  | 8.34 | 1251555.5556 | 4
C10201022700 |  | Door, single leaf, kd steel frame, metal fire, commercial quality, 3'-0" x 7'-0" x 1-3/8" | 222.22 |  | 2.76 | 414666.6667 | 4
C1030 |  | Fittings |  |  | 0.66 | 99496.32 | 3
C10307300100 |  | Partitions, hospital curtain, ceiling hung, poly oxford cloth | 2956.8 |  | 0.66 | 99496.32 | 4
C2010 |  | Stair Construction |  |  | 1.51 | 226200 | 3
C20101100720 |  | Stairs, steel, pan tread for conc in-fill, picket rail,12 risers w/ landing | 19.5 |  | 1.51 | 226200 | 4
C3010 |  | Wall Finishes |  |  | 5.6 | 839566.6667 | 3
C30102300140 |  | Painting, interior on plaster and drywall, walls & ceilings, roller work, primer & 2 coats | 180000 |  | 0.88 | 131400 | 4
C30102301940 |  | Ceramic tile, thin set, 4-1/4" x 4-1/4" | 116666.67 |  | 4.72 | 708166.6667 | 4
C3020 |  | Floor Finishes |  |  | 7.54 | 1130400 | 3
C30204100360 |  | Composition flooring, epoxy terrazzo, recycled porcelain | 15000 |  | 1.97 | 295500 | 4
C30204101120 |  | Terrazzo, maximum | 15000 |  | 2.76 | 414000 | 4
C30204101600 |  | Vinyl, composition tile, maximum | 90000 |  | 1.31 | 197100 | 4
C30204101720 |  | Tile, ceramic natural clay | 30000 |  | 1.49 | 223800 | 4
C3030 |  | Ceiling Finishes |  |  | 8.97 | 1345500 | 3
C30302106000 |  | Acoustic ceilings, 3/4" fiberglass board, 24" x 48" tile, tee grid, suspended support | 150000 |  | 8.97 | 1345500 | 4
D |  | Services |  | 52.63 | 108.64 | 16296425.9 | 1
D1010 |  | Elevators and Lifts |  |  | 7.18 | 1077750 | 3
D10101109250 |  | Traction, geared hospital, 6000 lb, 6 floors, 12' story height, 2 car group, 200 FPM | 4.5 |  | 7.18 | 1077750 | 4
D2010 |  | Plumbing Fixtures |  |  | 8.55 | 1282968.75 | 3
D20101102080 |  | Water closet, vitreous china, bowl only with flush valve, wall hung | 114.75 |  | 2.93 | 440066.25 | 4
D20102102000 |  | Urinal, vitreous china, wall hung | 38.25 |  | 0.35 | 51828.75 | 4
D20103102080 |  | Lavatory w/trim, wall hung, PE on CI, 19" x 17" | 114.75 |  | 1.62 | 243270 | 4
D20104102280 |  | Kitchen sink w/trim, raised deck, PE on CI, 42" x 21" dual level, triple bowl | 4.5 |  | 0.08 | 12487.5 | 4
D20104201840 |  | Laundry sink w/trim, PE on CI, black iron frame, 48" x 21" double compartment | 9 |  | 0.14 | 20340 | 4
D20104404300 |  | Service sink w/trim, PE on CI,wall hung w/rim guard, 22" x 18" | 9 |  | 0.31 | 46800 | 4
D20105102120 |  | Bathtub, recessed, PE on CI, mat bottom, 5'-6" long | 62.25 |  | 1.57 | 235305 | 4
D20107101680 |  | Shower, stall, baked enamel, terrazzo receptor, 36" square | 62.25 |  | 1.4 | 209471.25 | 4
D20108201920 |  | Water cooler, electric, wall hung, wheelchair type, 7.5 GPH | 9.75 |  | 0.16 | 23400 | 4
D2020 |  | Domestic Water Distribution |  |  | 10.64 | 1595311.875 | 3
D20202402420 |  | Electric water heater, commercial, 100 < F rise, 1000 gal, 480 KW 1970 GPH | 11.48 |  | 10.64 | 1595311.875 | 4
D2040 |  | Rain Water Drainage |  |  | 0.61 | 91575 | 3
D20402104280 |  | Roof drain, CI, soil,single hub, 5" diam, 10' high | 15 |  | 0.27 | 40425 | 4
D20402104320 |  | Roof drain, CI, soil,single hub, 5" diam, for each additional foot add | 930 |  | 0.34 | 51150 | 4
D3010 |  | Energy Supply |  |  | 5.34 | 801000 | 3
D30105600110 |  | Hot water reheat system for 200,000 SF hospital | 150000 |  | 5.34 | 801000 | 4
D3020 |  | Heat Generating Systems |  |  | 0.53 | 79640.625 | 3
D30201060900 |  | Boiler, electric, steel, steam, 510 KW, 1,740 MBH | 1.88 |  | 0.53 | 79640.625 | 4
D3030 |  | Cooling Generating Systems |  |  | 3.37 | 505200 | 3
D30301301020 |  | Chiller, reciprocating, water cooled, standard controls, 100 ton | 0.75 |  | 0.5 | 74850 | 4
D30301301030 |  | Chiller, reciprocating, water cooled, standard controls, 150 ton | 1.5 |  | 1.26 | 189000 | 4
D30301301040 |  | Chiller, reciprocating, water cooled, standard controls, 200 ton | 1.5 |  | 1.61 | 241350 | 4
D3090 |  | Other HVAC Systems/Equip |  |  | 40.91 | 6135862.5 | 3
D30905100210 |  | Ductwork for 200,000 SF hospital model | 240000 |  | 22.08 | 3312000 | 4
D30905101020 |  | Boiler, cast iron, gas, hot water, 2856 MBH | 3 |  | 1.69 | 253500 | 4
D30905101030 |  | Boiler, cast iron, gas, hot water, 320 MBH | 3 |  | 0.34 | 50475 | 4
D30905102010 |  | AHU, rooftop, cool/heat coils, VAV, filters, 5,000 CFM | 1.5 |  | 0.52 | 78300 | 4
D30905102020 |  | AHU, rooftop, cool/heat coils, VAV, filters, 10,000 CFM | 1.5 |  | 0.98 | 147450 | 4
D30905102030 |  | AHU, rooftop, cool/heat coils, VAV, filters, 20,000 CFM | 3 |  | 3.64 | 546000 | 4
D30905102040 |  | VAV terminal, cooling, hot water reheat, with actuator / controls, 200 CFM | 150 |  | 5.82 | 873750 | 4
D30905102045 |  | AHU, rooftop, cool/heat coils, VAV, filters, 30,000 CFM | 3 |  | 4.23 | 634500 | 4
D30905102060 |  | Roof vent. system, power, centrifugal, aluminum, galvanized curb, back draft damper, 1500 CFM | 1.5 |  | 0.09 | 12937.5 | 4
D30905102070 |  | Roof vent. system, power, centrifugal, aluminum, galvanized curb, back draft damper, 2750 CFM | 3 |  | 0.32 | 48300 | 4
D30905102080 |  | Roof vent. system, power, centrifugal, aluminum, galvanized curb, back draft damper, 5000 CFM | 0.75 |  | 0.3 | 44400 | 4
D30905102090 |  | Plate heat exchanger, 400 GPM | 1.5 |  | 0.9 | 134250 | 4
D4010 |  | Sprinklers |  |  | 2.79 | 418760.625 | 3
D40104100620 |  | Wet pipe sprinkler systems, steel, light hazard, 1 floor, 10,000 SF | 25500 |  | 0.6 | 89250 | 4
D40104100740 |  | Wet pipe sprinkler systems, steel, light hazard, each additional floor, 10,000 SF | 124500 |  | 2.14 | 321210 | 4
D40104108940 |  | Standard High Rise Accessory Package 8 story | 0.71 |  | 0.06 | 8300.625 | 4
D4020 |  | Standpipes |  |  | 0.69 | 104109 | 3
D40203101540 |  | Wet standpipe risers, class III, steel, black, sch 40, 4" diam pipe, 1 floor | 1.8 |  | 0.13 | 19710 | 4
D40203101560 |  | Wet standpipe risers, class III, steel, black, sch 40, 4" diam pipe, additional floors | 9.3 |  | 0.16 | 23808 | 4
D40204100900 |  | Cabs, hose rack assembly, & extinguisher, 2-1/2" x 1-1/2" valve & hose, steel door & frame | 9 |  | 0.03 | 4716 | 4
D40204101650 |  | Alarm, electric pressure switch (circuit closer) | 18 |  | 0.02 | 2763 | 4
D40204103050 |  | Escutcheon plate, for angle valves, polished brass, 2-1/2" | 9 |  | 0 | 337.5 | 4
D40204103650 |  | Fire pump, electric, with controller, 5" pump, 100 HP, 1000 GPM | 0.9 |  | 0.26 | 39015 | 4
D40204103700 |  | Fire pump, electric, for jockey pump system, add | 0.9 |  | 0.03 | 4590 | 4
D40204107050 |  | Siamese, with plugs & chains, polished brass, sidewalk, 4" x 2-1/2" x 2-1/2" | 1.5 |  | 0.01 | 1815 | 4
D40204108050 |  | Valves, angle, wheel handle, 300 lb, 2-1/2" | 19.5 |  | 0.04 | 5869.5 | 4
D40204108400 |  | Cabinet assembly, includes. adapter, rack, hose, and nozzle | 0.75 |  | 0.01 | 1485 | 4
D5010 |  | Electrical Service/Distribution |  |  | 3.54 | 531650 | 3
D50101301000 |  | Underground service installation, includes excavation, backfill, and compaction, 100' length, 4' depth, 3 phase, 4 wire, 277/480 volts, 2000 A | 2 |  | 1.07 | 160400 | 4
D50102300360 |  | Feeder installation 600 V, including RGS conduit and XHHW wire, 600 A | 200 |  | 0.23 | 33900 | 4
D50102300560 |  | Feeder installation 600 V, including RGS conduit and XHHW wire, 2000 A | 400 |  | 1.43 | 214400 | 4
D50102400620 |  | Switchgear installation, incl switchboard, panels & circuit breaker, 277/480 V, 2000 A | 2 |  | 0.82 | 122950 | 4
D5020 |  | Lighting and Branch Wiring |  |  | 21.44 | 3216127.5 | 3
D50201100720 |  | Receptacles incl plate, box, conduit, wire, 20 per 1000 SF,2.4 W per SF, with transformer | 262500 |  | 9.43 | 1414875 | 4
D50201300360 |  | Wall switches, 5.0 per 1000 SF | 262500 |  | 2.22 | 333375 | 4
D50201350320 |  | Miscellaneous power, 1.2 watts | 450000 |  | 1.05 | 157500 | 4
D50201400280 |  | Central air conditioning power, 4 watts | 189000 |  | 0.83 | 124740 | 4
D50201452080 |  | Motor installation, three phase, 460 V, 15 HP motor size | 15 |  | 0.24 | 35850 | 4
D50201550440 |  | Motor feeder systems, three phase, feed to 200 V 5 HP, 230 V 7.5 HP, 460 V 15 HP, 575 V 20 HP | 750 |  | 0.06 | 8587.5 | 4
D50202100500 |  | Fluorescent fixtures recess mounted in ceiling, 0.8 watt per SF, 20 FC, 5 fixtures @32 watt per 1000 SF | 360000 |  | 7.61 | 1141200 | 4
D5030 |  | Communications and Security |  |  | 2.03 | 304715.625 | 3
D50309100456 |  | Communication and alarm systems, fire detection, addressable, 100 detectors, includes outlets, boxes, conduit and wire | 3.75 |  | 1.93 | 289500 | 4
D50309100462 |  | Fire alarm command center, addressable with voice, excl. wire & conduit | 1.12 |  | 0.1 | 15215.625 | 4
D50309200110 |  | Internet wiring, 8 data/voice outlets per 1000 S.F. | 1 |  | 0 | 0 | 4
D5090 |  | Other Electrical Systems |  |  | 1.01 | 151754.4 | 3
D50902100680 |  | Generator sets, w/battery, charger, muffler and transfer switch, diesel engine with fuel tank, 100 kW | 0.9 |  | 0 | 356.4 | 4
D50902101000 |  | Generator sets, w/battery, charger, muffler and transfer switch, diesel engine with fuel tank, 400 kW | 651 |  | 1.01 | 151032 | 4
D50902200300 |  | Uninterruptible power supply with standard battery pack, 15 kVA/12.75 kW | 300 |  | 0 | 366 | 4
E |  | Equipment & Furnishings |  | 13.36 | 27.58 | 4136856 | 1
E1020 |  | Institutional Equipment |  |  | 23.36 | 3503293.5 | 3
E10207100110 |  | Architectural equipment, laboratory equipment glassware washer, distilled water, economy | 2.25 |  | 0.13 | 19125 | 4
E10207100160 |  | Architectural equipment, sink, epoxy resin, 25" x 16" x 10" | 4.5 |  | 0.06 | 9135 | 4
E10207100170 |  | Architectural equipment, laboratory equipment eye wash, hand held | 4.5 |  | 0.01 | 2182.5 | 4
E10207105000 |  | Fume hood, complex, including fixtures and ductwork | 4.5 |  | 0.67 | 100125 | 4
E10208100730 |  | Architectural equipment, medical equipment sterilizers, floor loading, double door, 28"x67"x52" | 3.75 |  | 6.16 | 924375 | 4
E10208200120 |  | Architectural equipment, medical equipment, medical gas system for large hospital | 300000 |  | 13.06 | 1959000 | 4
E10209100130 |  | Architectural equipment, kitchen equipment, commercial dish washer, semiautomatic, 50 racks/hr | 1.5 |  | 0.09 | 13492.5 | 4
E10209100160 |  | Architectural equipment, kitchen equipment, food warmer, counter, 1.65 KW | 4.5 |  | 0.02 | 3172.5 | 4
E10209100190 |  | Architectural equipment, kitchen equipment, kettles, steam jacketed, 20 gallons | 3 |  | 0.29 | 43242 | 4
E10209100200 |  | Architectural equipment, kitchen equipment, range, restaurant type, burners, 2 ovens & 24" griddle | 3 |  | 0.1 | 15699 | 4
E10209100210 |  | Architectural equipment, kitchen equipment, range hood, including CO2 system, economy | 3 |  | 0.05 | 7845 | 4
E10209100310 |  | Special construction, refrigerators, prefabricated, walk-in, 7'-6" high, 6' x 6' | 3000 |  | 2.71 | 405900 | 4
E1090 |  | Other Equipment |  |  | 0 | 0 | 3
E2020 |  | Moveable Furnishings |  |  | 4.22 | 633562.5 | 3
E20202100250 |  | Furnishings, hospital furniture, patient wall system, no utilities, deluxe , per room | 232.5 |  | 4.22 | 633562.5 | 4
F |  | Special Construction |  | 0 | 0 | 0 | 1
G |  | Building Sitework |  | 0 | 0 | 0 | 1
SubTotal |  |  |  | 100% | $206.44 | $30,966,500.41
Contractor Fees (General Conditions,Overhead,Profit) |  |  |  | 25.0% | $51.61 | $7,741,625.10
Architectural Fees |  |  |  | 9.0% | $23.22 | $3,483,731.30
User Fees |  |  |  | 0.0% | $0.00 | $0.00
Total Building Cost |  |  |  |  | $281.28 | $42,191,856.80
Audit Trail Notes
Date Time | Description |  |  | User Name |  | Action