## Squarefoot_Estimate
|  | Square Foot Cost Estimate Report |  |  | Date: | 11/12/2022
Estimate Name: |  | office
Building Type: |  | Hospital, 2-3 Story with Curtain Wall / Rigid Steel
Location: |  | NATIONAL AVERAGE
Story Count: |  | 3
Story Height (L.F.): |  | 10
Floor Area (S.F.): |  | 166750
Labor Type: |  | OPN
Basement Included: |  | No | [5 empty] | Assembly Customization Type:
Data Release: |  | Year 2022 | Costs are derived from a building model with basic components. | [5 empty] | Added
Cost Per Square Foot: |  | $327.19 | Scope differences and market conditions can cause costs to vary significantly. | [5 empty] | Partially Swapped
Building Cost: |  | $54,558,333.71 | [6 empty] | Fully Swapped
|  |  | Quantity | % of Total | Cost Per S.F. | Cost
A |  | Substructure |  | 1.24 | 2.97 | 495557.6515 | 1
A1010 |  | Standard Foundations |  |  | 0.93 | 154831.8182 | 3
A10101051560 |  | Foundation wall, CIP, 4' wall height, direct chute, .148 CY/LF, 7.2 PLF, 12" thick | 476 |  | 0.25 | 40936 | 4
A10101103100 |  | Strip footing, concrete, reinforced, load 14.8 KLF, soil bearing capacity 6 KSF, 12" deep x 32" wide | 523.6 |  | 0.16 | 27489 | 4
A10102107700 |  | Spread footings, 3000 PSI concrete, load 200K, soil bearing capacity 6 KSF, 6' - 0" square x 20" deep | 90.95 |  | 0.52 | 86406.8182 | 4
A1030 |  | Slab on Grade |  |  | 1.98 | 330720.8333 | 3
A10301202240 |  | Slab on grade, 4" thick, non industrial, reinforced | 55583.33 |  | 1.98 | 330720.8333 | 4
A2010 |  | Basement Excavation |  |  | 0.06 | 10005 | 3
A20101105740 |  | Excavate and fill, 30,000 SF, 4' deep, sand, gravel, or common earth, on site storage | 55583.33 |  | 0.06 | 10005 | 4
B |  | Shell |  | 8.7 | 20.9 | 3485176.8487 | 1
B1010 |  | Floor Construction |  |  | 9.94 | 1658193.042 | 3
B10102481720 |  | Floor, concrete, slab form, open web bar joist @ 2' OC, on W beam and wall, 25'x25' bay, 23" deep, 40 PSF superimposed load, 84 PSF total load | 111166.67 |  | 9.33 | 1555221.6667 | 4
B10102481730 |  | Floor, concrete, slab form, open web bar joist @ 2' OC, on W beam and wall, 25'x25' bay, 23" deep, 40 PSF superimposed load, 84 PSF total load, for columns add | 111166.67 |  | 0.41 | 68923.3333 | 4
B10107203700 |  | Fireproofing, gypsum board, fire rated, 2 layer, 1" thick, 14" steel column, 3 hour rating, 22 PLF | 909.16 |  | 0.2 | 34048.042 | 4
B1020 |  | Roof Construction |  |  | 3.94 | 656439.1667 | 3
B10201123300 |  | Roof, steel joists, beams, 1.5" 22 ga metal deck, on columns, 25'x25' bay, 20" deep, 40 PSF superimposed load, 60 PSF total load | 55583.33 |  | 3.24 | 540270 | 4
B10201123400 |  | Roof, steel joists, beams, 1.5" 22 ga metal deck, on columns, 25'x25' bay, 20" deep, 40 PSF superimposed load, 60 PSF total load, add for column | 55583.33 |  | 0.7 | 116169.1667 | 4
B2020 |  | Exterior Windows |  |  | 4.16 | 694136.52 | 3
B20202102000 |  | Aluminum flush tube frame, thermo-break frame, 2.25" x 4.5", 5'x6' opening, no intermediate horizontals | 14137.2 |  | 2.49 | 414926.82 | 4
B20202202000 |  | Glazing panel, plate glass, 1/4" thick, clear | 14137.2 |  | 1.67 | 279209.7 | 4
B2030 |  | Exterior Doors |  |  | 0.53 | 88862.5909 | 3
B20301106950 |  | Door, aluminum & glass, with transom, narrow stile, double door, hardware, 6'-0" x 10'-0" opening | 6.06 |  | 0.28 | 46235.2273 | 4
B20302203500 |  | Door, steel 18 gauge, hollow metal, 1 door with frame, no label, 3'-6" x 7'-0" opening | 12.13 |  | 0.26 | 42627.3636 | 4
B3010 |  | Roof Coverings |  |  | 2.11 | 351212.22 | 3
B30101203400 |  | Roofing, single ply membrane, EPDM, 60 mils, loosely laid, stone ballast | 55583.33 |  | 0.59 | 98382.5 | 4
B30103202700 |  | Insulation, rigid, roof deck, extruded polystyrene, 40 PSI compressive strength, 4" thick, R20 | 55583.33 |  | 1.38 | 230115 | 4
B30104201400 |  | Roof edges, aluminum, duranodic, .050" thick, 6" face | 476 |  | 0.08 | 14161 | 4
B30104300040 |  | Flashing, aluminum, no backing sides, .019" | 476 |  | 0.03 | 4364.92 | 4
B30106305100 |  | Gravel stop, aluminum, extruded, 4", mill finish, .050" thick | 476 |  | 0.03 | 4188.8 | 4
B3020 |  | Roof Openings |  |  | 0.22 | 36333.3091 | 3
B30202100300 |  | Roof hatch, with curb, 1" fiberglass insulation, 2'-6" x 3'-0", galvanized steel, 165 lbs | 12.13 |  | 0.1 | 16396.0727 | 4
B30202102100 |  | Smoke hatch, unlabeled, galvanized, 2'-6" x 3', not incl hand winch operator | 12.13 |  | 0.12 | 19937.2364 | 4
C |  | Interiors |  | 18.02 | 43.27 | 7214475.3979 | 1
C1010 |  | Partitions |  |  | 7.22 | 1204305.5556 | 3
C10101045500 |  | Concrete block (CMU) partition, light weight, hollow, 6" thick, no finish | 18527.78 |  | 0.91 | 151186.6667 | 4
C10101265425 |  | Metal partition, 5/8"fire rated gypsum board face, no base,3 -5/8" @ 24" OC framing, same opposite face, sound attenuation insulation | 166750 |  | 5.54 | 923795 | 4
C10101280850 |  | Gypsum board, 1 face only, 5/8" with 1/16" lead | 7411.11 |  | 0.78 | 129323.8889 | 4
C1020 |  | Interior Doors |  |  | 11.11 | 1852283.7037 | 3
C10201022600 |  | Door, single leaf, kd steel frame, hollow metal, commercial quality, flush, 3'-0" x 7'-0" x 1-3/8" | 988.15 |  | 8.34 | 1391312.5926 | 4
C10201022700 |  | Door, single leaf, kd steel frame, metal fire, commercial quality, 3'-0" x 7'-0" x 1-3/8" | 247.04 |  | 2.76 | 460971.1111 | 4
C1030 |  | Fittings |  |  | 0.34 | 56541.422 | 3
C10307300100 |  | Partitions, hospital curtain, ceiling hung, poly oxford cloth | 1680.28 |  | 0.34 | 56541.422 | 4
C2010 |  | Stair Construction |  |  | 1.24 | 206770 | 3
C20101100600 |  | Stairs, CIP concrete, w/landing, 20 risers, with nosing | 24.25 |  | 1.24 | 206770 | 4
C3010 |  | Wall Finishes |  |  | 6.45 | 1076332.9667 | 3
C30102202000 |  | 2 coats paint on masonry with block filler | 37055.56 |  | 0.66 | 109313.8889 | 4
C30102202000 |  | 2 coats paint on masonry with block filler | 11424 |  | 0.2 | 33700.8 | 4
C30102300140 |  | Painting, interior on plaster and drywall, walls & ceilings, roller work, primer & 2 coats | 200100 |  | 0.88 | 146073 | 4
C30102301940 |  | Ceramic tile, thin set, 4-1/4" x 4-1/4" | 129694.44 |  | 4.72 | 787245.2778 | 4
C3020 |  | Floor Finishes |  |  | 7.93 | 1322494.25 | 3
C30204100360 |  | Composition flooring, epoxy terrazzo, recycled porcelain | 8337.5 |  | 0.98 | 164248.75 | 4
C30204101120 |  | Terrazzo, maximum | 25012.5 |  | 4.14 | 690345 | 4
C30204101600 |  | Vinyl, composition tile, maximum | 100050 |  | 1.31 | 219109.5 | 4
C30204101720 |  | Tile, ceramic natural clay | 33350 |  | 1.49 | 248791 | 4
C3030 |  | Ceiling Finishes |  |  | 8.97 | 1495747.5 | 3
C30302106000 |  | Acoustic ceilings, 3/4" fiberglass board, 24" x 48" tile, tee grid, suspended support | 166750 |  | 8.97 | 1495747.5 | 4
D |  | Services |  | 52.72 | 126.59 | 21109348.7614 | 1
D1010 |  | Elevators and Lifts |  |  | 5.28 | 880440 | 3
D10101108800 |  | Hydraulic hospital elevator, 4000 lb., 3 floors, 12 FT story height, 125 FPM | 6.06 |  | 5.28 | 880440 | 4
D2010 |  | Plumbing Fixtures |  |  | 9.17 | 1529324.8864 | 3
D20101102080 |  | Water closet, vitreous china, bowl only with flush valve, wall hung | 127.34 |  | 2.93 | 488334.9545 | 4
D20102102000 |  | Urinal, vitreous china, wall hung | 42.45 |  | 0.34 | 57513.5909 | 4
D20103102080 |  | Lavatory w/trim, wall hung, PE on CI, 19" x 17" | 127.34 |  | 1.62 | 269953.0909 | 4
D20104102280 |  | Kitchen sink w/trim, raised deck, PE on CI, 42" x 21" dual level, triple bowl | 18.19 |  | 0.3 | 50479.7727 | 4
D20104201840 |  | Laundry sink w/trim, PE on CI, black iron frame, 48" x 21" double compartment | 18.19 |  | 0.25 | 41111.4545 | 4
D20104404300 |  | Service sink w/trim, PE on CI,wall hung w/rim guard, 22" x 18" | 18.19 |  | 0.57 | 94592.7273 | 4
D20105102120 |  | Bathtub, recessed, PE on CI, mat bottom, 5'-6" long | 69.73 |  | 1.58 | 263586.2727 | 4
D20107101680 |  | Shower, stall, baked enamel, terrazzo receptor, 36" square | 69.73 |  | 1.41 | 234647.5682 | 4
D20108201920 |  | Water cooler, electric, wall hung, wheelchair type, 7.5 GPH | 12.13 |  | 0.17 | 29105.4545 | 4
D2020 |  | Domestic Water Distribution |  |  | 17.45 | 2909613.1705 | 3
D20202402180 |  | Electric water heater, commercial, 100 < F rise, 350 gal, 180 KW 738 GPH | 46.39 |  | 17.45 | 2909613.1705 | 4
D2040 |  | Rain Water Drainage |  |  | 0.6 | 100050 | 3
D20402104280 |  | Roof drain, CI, soil,single hub, 5" diam, 10' high | 24.25 |  | 0.39 | 65366 | 4
D20402104320 |  | Roof drain, CI, soil,single hub, 5" diam, for each additional foot add | 630.62 |  | 0.21 | 34684 | 4
D3010 |  | Energy Supply |  |  | 6.13 | 1022177.5 | 3
D30105600100 |  | Hot water reheat system for 55,000 SF hospital | 166750 |  | 6.13 | 1022177.5 | 4
D3020 |  | Heat Generating Systems |  |  | 3.78 | 629557.0455 | 3
D30201301020 |  | Boiler, cast iron, gas, hot water, 200 MBH | 3.03 |  | 0.33 | 55027.5 | 4
D30201301100 |  | Boiler, cast iron, gas, hot water, 2856 MBH | 3.03 |  | 1.54 | 256188.6364 | 4
D30203301030 |  | Pump, base mounted with motor, end-suction, 4" size, 7-1/2 HP, to 350 GPM | 12.13 |  | 1.91 | 318340.9091 | 4
D3030 |  | Cooling Generating Systems |  |  | 7 | 1166567.8409 | 3
D30301301010 |  | Chiller, reciprocating, water cooled, standard controls, 60 ton | 6.06 |  | 2.35 | 392317.2727 | 4
D30301301030 |  | Chiller, reciprocating, water cooled, standard controls, 150 ton | 3.03 |  | 2.29 | 382009.0909 | 4
D30303101010 |  | Cooling tower, galvanized steel, packaged unit, draw thru, 60 ton | 3.03 |  | 0.66 | 109676.0227 | 4
D30303101020 |  | Cooling tower, galvanized steel, packaged unit, draw thru, 110 ton | 6.06 |  | 1.69 | 282565.4545 | 4
D3090 |  | Other HVAC Systems/Equip |  |  | 45.29 | 7552107.5 | 3
D30905100200 |  | Ductwork for 55,000 SF Surgery center | 166750 |  | 17.9 | 2984825 | 4
D30905102010 |  | AHU, rooftop, cool/heat coils, VAV, filters, 5,000 CFM | 3.03 |  | 0.95 | 158260.9091 | 4
D30905102020 |  | AHU, rooftop, cool/heat coils, VAV, filters, 10,000 CFM | 6.06 |  | 3.57 | 596055.4545 | 4
D30905102030 |  | AHU, rooftop, cool/heat coils, VAV, filters, 20,000 CFM | 12.13 |  | 13.24 | 2207163.6364 | 4
D30905102040 |  | VAV terminal, cooling, hot water reheat, with actuator / controls, 200 CFM | 166.75 |  | 5.82 | 971318.75 | 4
D30905102050 |  | Roof vent. system, centrifugal, aluminum, galvanized curb, back draft damper, 500 CFM | 3.03 |  | 0.07 | 11066.1364 | 4
D30905102060 |  | Roof vent. system, power, centrifugal, aluminum, galvanized curb, back draft damper, 1500 CFM | 3.03 |  | 0.16 | 26149.4318 | 4
D30905102070 |  | Roof vent. system, power, centrifugal, aluminum, galvanized curb, back draft damper, 2750 CFM | 9.1 |  | 0.88 | 146436.8182 | 4
D30905102080 |  | Roof vent. system, power, centrifugal, aluminum, galvanized curb, back draft damper, 5000 CFM | 3.03 |  | 1.08 | 179483.6364 | 4
D30905102090 |  | Plate heat exchanger, 400 GPM | 3.03 |  | 1.63 | 271347.7273 | 4
D4010 |  | Sprinklers |  |  | 2.99 | 498349.05 | 3
D40104100620 |  | Wet pipe sprinkler systems, steel, light hazard, 1 floor, 10,000 SF | 55027.5 |  | 1.16 | 192596.25 | 4
D40104100740 |  | Wet pipe sprinkler systems, steel, light hazard, each additional floor, 10,000 SF | 111722.5 |  | 1.73 | 288244.05 | 4
D40104108930 |  | Standard High Rise Accessory Package 3 story | 3.03 |  | 0.1 | 17508.75 | 4
D4020 |  | Standpipes |  |  | 0.97 | 161950.6318 | 3
D40203101540 |  | Wet standpipe risers, class III, steel, black, sch 40, 4" diam pipe, 1 floor | 7.28 |  | 0.48 | 79676.1818 | 4
D40203101560 |  | Wet standpipe risers, class III, steel, black, sch 40, 4" diam pipe, additional floors | 15.77 |  | 0.24 | 40359.5636 | 4
D40204100900 |  | Cabs, hose rack assembly, & extinguisher, 2-1/2" x 1-1/2" valve & hose, steel door & frame | 18.19 |  | 0.06 | 9532.0364 | 4
D40204101650 |  | Alarm, electric pressure switch (circuit closer) | 36.38 |  | 0.03 | 5584.6091 | 4
D40204103050 |  | Escutcheon plate, for angle valves, polished brass, 2-1/2" | 18.19 |  | 0 | 682.1591 | 4
D40204107050 |  | Siamese, with plugs & chains, polished brass, sidewalk, 4" x 2-1/2" x 2-1/2" | 6.06 |  | 0.04 | 7337 | 4
D40204108050 |  | Valves, angle, wheel handle, 300 lb, 2-1/2" | 42.45 |  | 0.08 | 12776.0818 | 4
D40204108400 |  | Cabinet assembly, includes. adapter, rack, hose, and nozzle | 3.03 |  | 0.04 | 6003 | 4
D5010 |  | Electrical Service/Distribution |  |  | 1.06 | 176300 | 3
D50101301400 |  | Underground service installation, includes excavation, backfill, and compaction, 100' length, 4' depth, 3 phase, 4 wire, 277/480 volts, 800 A | 2.25 |  | 0.49 | 81900 | 4
D50102300400 |  | Feeder installation 600 V, including RGS conduit and XHHW wire, 800 A | 200 |  | 0.25 | 42200 | 4
D50102400540 |  | Switchgear installation, incl switchboard, panels & circuit breaker, 277/480 V, 800 A | 2 |  | 0.31 | 52200 | 4
D5020 |  | Lighting and Branch Wiring |  |  | 17.86 | 2978865.55 | 3
D50201100720 |  | Receptacles incl plate, box, conduit, wire, 20 per 1000 SF,2.4 W per SF, with transformer | 250125 |  | 8.08 | 1348173.75 | 4
D50201300360 |  | Wall switches, 5.0 per 1000 SF | 250125 |  | 1.9 | 317658.75 | 4
D50201350320 |  | Miscellaneous power, 1.2 watts | 250125 |  | 0.52 | 87543.75 | 4
D50201400280 |  | Central air conditioning power, 4 watts | 210105 |  | 0.83 | 138669.3 | 4
D50201452080 |  | Motor installation, three phase, 460 V, 15 HP motor size | 10 |  | 0.14 | 23900 | 4
D50201550440 |  | Motor feeder systems, three phase, feed to 200 V 5 HP, 230 V 7.5 HP, 460 V 15 HP, 575 V 20 HP | 500 |  | 0.03 | 5725 | 4
D50202100500 |  | Fluorescent fixtures recess mounted in ceiling, 0.8 watt per SF, 20 FC, 5 fixtures @32 watt per 1000 SF | 333500 |  | 6.34 | 1057195 | 4
D5030 |  | Communications and Security |  |  | 5.59 | 932469.0318 | 3
D50309100456 |  | Communication and alarm systems, fire detection, addressable, 100 detectors, includes outlets, boxes, conduit and wire | 4.55 |  | 2.11 | 351084.5455 | 4
D50309100462 |  | Fire alarm command center, addressable with voice, excl. wire & conduit | 3.03 |  | 0.25 | 41005.3409 | 4
D50309100600 |  | Communication and alarm systems, includes outlets, boxes, conduit and wire, intercom systems, 50 stations | 4.85 |  | 2.39 | 399229.8182 | 4
D50309101000 |  | Communication and alarm systems, includes outlets, boxes, conduit and wire, master TV antenna systems, 30 outlets | 3.43 |  | 0.85 | 141149.3273 | 4
D50309200110 |  | Internet wiring, 8 data/voice outlets per 1000 S.F. | 1 |  | 0 | 0 | 4
D5090 |  | Other Electrical Systems |  |  | 3.43 | 571576.5545 | 3
D50902100840 |  | Generator sets, w/battery, charger, muffler and transfer switch, diesel engine with fuel tank, 200 kW | 1625.05 |  | 3.43 | 571206.6727 | 4
D50902200300 |  | Uninterruptible power supply with standard battery pack, 15 kVA/12.75 kW | 303.18 |  | 0 | 369.8818 | 4
E |  | Equipment & Furnishings |  | 19.32 | 46.41 | 7738255.0727 | 1
E1020 |  | Institutional Equipment |  |  | 42.19 | 7036010.1864 | 3
E10207100110 |  | Architectural equipment, laboratory equipment glassware washer, distilled water, economy | 6.06 |  | 0.31 | 51540.9091 | 4
E10207100160 |  | Architectural equipment, sink, epoxy resin, 25" x 16" x 10" | 6.06 |  | 0.07 | 12309.1818 | 4
E10207100170 |  | Architectural equipment, laboratory equipment eye wash, hand held | 9.1 |  | 0.03 | 4411.2955 | 4
E10207105000 |  | Fume hood, complex, including fixtures and ductwork | 24.25 |  | 3.24 | 539663.6364 | 4
E10208100730 |  | Architectural equipment, medical equipment sterilizers, floor loading, double door, 28"x67"x52" | 3.03 |  | 4.48 | 747343.1818 | 4
E10208100800 |  | Architectural equipment, medical equipment, X-ray, stationary, deluxe | 6.06 |  | 9.87 | 1646277.2727 | 4
E10208200110 |  | Architectural equipment, medical equipment, medical gas system for small hospital | 333500 |  | 19.44 | 3241620 | 4
E10209100130 |  | Architectural equipment, kitchen equipment, commercial dish washer, semiautomatic, 50 racks/hr | 6.06 |  | 0.33 | 54542.4091 | 4
E10209100160 |  | Architectural equipment, kitchen equipment, food warmer, counter, 1.65 KW | 24.25 |  | 0.1 | 17099.4545 | 4
E10209100190 |  | Architectural equipment, kitchen equipment, kettles, steam jacketed, 20 gallons | 12.13 |  | 1.05 | 174802.5091 | 4
E10209100200 |  | Architectural equipment, kitchen equipment, range, restaurant type, burners, 2 ovens & 24" griddle | 12.13 |  | 0.38 | 63462.0182 | 4
E10209100210 |  | Architectural equipment, kitchen equipment, range hood, including CO2 system, economy | 12.13 |  | 0.19 | 31712.8182 | 4
E10209100310 |  | Special construction, refrigerators, prefabricated, walk-in, 7'-6" high, 6' x 6' | 3335 |  | 2.71 | 451225.5 | 4
E1090 |  | Other Equipment |  |  | 0 | 0 | 3
E2020 |  | Moveable Furnishings |  |  | 4.21 | 702244.8864 | 3
E20202100250 |  | Furnishings, hospital furniture, patient wall system, no utilities, deluxe , per room | 257.7 |  | 4.21 | 702244.8864 | 4
F |  | Special Construction |  | 0 | 0 | 0 | 1
G |  | Building Sitework |  | 0 | 0 | 0 | 1
SubTotal |  |  |  | 100% | $240.14 | $40,042,813.73
Contractor Fees (General Conditions,Overhead,Profit) |  |  |  | 25.0% | $60.03 | $10,010,703.43
Architectural Fees |  |  |  | 9.0% | $27.02 | $4,504,816.54
User Fees |  |  |  | 0.0% | $0.00 | $0.00
Total Building Cost |  |  |  |  | $327.19 | $54,558,333.71
Audit Trail Notes
Date Time | Description |  |  | User Name |  | Action