## Squarefoot_Estimate
|  | Square Foot Cost Estimate Report |  |  | Date: | 10/31/2022
Estimate Name: |  | office
Building Type: |  | Office, 11-20 Story (Green) with Curtain Wall / Rigid Steel
Location: |  | NATIONAL AVERAGE
Story Count: |  | 15
Story Height (L.F.): |  | 10.00
Floor Area (S.F.): |  | 715500
Labor Type: |  | OPN
Basement Included: |  | No | [5 empty] | Assembly Customization Type:
Data Release: |  | Year 2022 | Costs are derived from a building model with basic components. | [5 empty] | Added
Cost Per Square Foot: |  | $157.02 | Scope differences and market conditions can cause costs to vary significantly. | [5 empty] | Partially Swapped
Building Cost: |  | $112,350,883.89 | [6 empty] | Fully Swapped
|  |  | Quantity | % of Total | Cost Per S.F. | Cost
A |  | Substructure |  | 4.2 | 4.98 | 3563514.6231 | 1
A1010 |  | Standard Foundations |  |  | 0.8 | 569372.8846 | 3
A10102506350 |  | Pile caps, 12 piles, 11' - 6" x 8' - 6" x 49", 40 ton capacity, 19" column size, 900 K column | 55.04 |  | 0.38 | 271064.4231 | 4
A10102506600 |  | Pile caps, 14 piles, 11' - 6" x 10' - 9" x 55", 80 ton capacity, 29"column size, 2155 K column | 44.03 |  | 0.42 | 298308.4615 | 4
A1020 |  | Special Foundations |  |  | 3.62 | 2592077.5385 | 3
A10201402420 |  | Steel H piles, 50' long, 800K load, end bearing, 12 pile cluster | 55.04 |  | 1.92 | 1371833.6538 | 4
A10201402500 |  | Steel H piles, 50' long, 1600K load, end bearing, 10 pile cluster | 44.03 |  | 1.57 | 1123885.3846 | 4
A10202104620 |  | Grade beam, 30' span, 52" deep, 14" wide, 12 KLF load | 441 |  | 0.13 | 96358.5 | 4
A1030 |  | Slab on Grade |  |  | 0.4 | 285723 | 3
A10301209000 |  | Slab on grade, 4" thick, non industrial, reinforced, recycled plastic vapor barrier | 47700 |  | 0.4 | 285723 | 4
A2010 |  | Basement Excavation |  |  | 0.02 | 15264 | 3
A20101104560 |  | Excavate and fill, 10,000 SF, 4' deep, sand, gravel, or common earth, on site storage | 47700 |  | 0.02 | 15264 | 4
A2020 |  | Basement Walls |  |  | 0.14 | 101077.2 | 3
A20201111560 |  | Foundation wall, CIP, 4' wall height, direct chute, .148 CY/LF, 7.2 PLF, 12" thick, 3" XPS R15 | 1058.4 |  | 0.14 | 101077.2 | 4
B |  | Shell |  | 33.5 | 39.7 | 28402242.9702 | 1
B1010 |  | Floor Construction |  |  | 29.81 | 21328529.4194 | 3
B10102081600 |  | Steel column, W5, 50 K, 10' unsupported length, 16 PLF | 440.31 |  | 0.03 | 19989.9692 | 4
B10102084800 |  | Steel column, W10, 200 KIPS, 16' unsupported height, 49 PLF | 1210.85 |  | 0.18 | 129318.3692 | 4
B10102085400 |  | Steel column, W12, 300 KIPS, 16' unsupported height, 72 PLF | 968.68 |  | 0.21 | 148013.8338 | 4
B10102086000 |  | Steel column, W12, 400 KIPS, 16' unsupported height, 87 PLF | 1210.85 |  | 0.31 | 221342.6769 | 4
B10102086600 |  | Steel column, TS14, 500 KIPS, 16' unsupported height, 109 PLF | 1210.85 |  | 0.39 | 275830.7538 | 4
B10102087800 |  | Steel column, W14, 700 KIPS, 16' unsupported height, 145 PLF | 1210.85 |  | 0.51 | 363011.6769 | 4
B10102088300 |  | Steel column, W14, 800 KIPS, 16' unsupported height, 159 PLF | 1210.85 |  | 0.55 | 396915.3692 | 4
B10102089200 |  | Steel column, W14, 1000 KIPS, 16' unsupported height, 193 PLF | 2999.6 |  | 1.67 | 1193239.35 | 4
B10102524300 |  | Floor, composite concrete slab on fireproofed W beam, 4.5" slab, 25'x25' bay, 20.5" total depth, 75 PSF superimposed load, 136 PSF total | 667800 |  | 25.81 | 18464670 | 4
B10107203900 |  | Fireproofing, sprayed fiber, 1.5" thick, 8" steel column, 2 hour rating, 6.3 PLF | 8398.87 |  | 0.13 | 92723.5163 | 4 | 10050.03
B10107204050 |  | Fireproofing, sprayed fiber, 1.5" thick, 10" steel column, 2 hour rating, 7.9 PLF | 1210.85 |  | 0.02 | 16164.7962 | 4 | 0.2107
B10107204200 |  | Fireproofing, sprayed fiber, 1.5" thick, 14" steel column, 2 hour rating,10.8 PLF | 440.31 |  | 0.01 | 7309.1077 | 4 | 0.014
B1020 |  | Roof Construction |  |  | 0.65 | 463644 | 3
B10201123300 |  | Roof, steel joists, beams, 1.5" 22 ga metal deck, on columns, 25'x25' bay, 20" deep, 40 PSF superimposed load, 60 PSF total load | 47700 |  | 0.65 | 463644 | 4
B2020 |  | Exterior Windows |  |  | 7.93 | 5671965.6 | 3
B20202102000 |  | Aluminum flush tube frame, thermo-break frame, 2.25" x 4.5", 5'x6' opening, no intermediate horizontals | 66150 |  | 2.71 | 1941502.5 | 4
B20202201700 |  | Glazing panel, insulating, 1" thick units, 2 lites, light and heat reflective glass, tinted | 66150 |  | 5.15 | 3687862.5 | 4
B20202209000 |  | Curtain wall insulation and finishing, 3" R15 rigid insulation, metal furring 24" oc, gypsum board 5/8" thick | 6615 |  | 0.06 | 42600.6 | 4
B2030 |  | Exterior Doors |  |  | 0.87 | 621384.2308 | 3
B20301106550 |  | Door, aluminum & glass, without transom, full vision, double door, hardware, 6'-0" x 7'-0" opening | 44.03 |  | 0.46 | 329130 | 4
B20301107250 |  | Door, aluminum & glass, with transom, non-standard, double door, hardware, 6'-0" x 10'-0" opening | 33.02 |  | 0.41 | 292254.2308 | 4
B3010 |  | Roof Coverings |  |  | 0.44 | 316719.72 | 3
B30101206200 |  | Roofing, single ply membrane, reinforced, PVC, 48 mils, fully adhered, adhesive | 47700 |  | 0.14 | 102078 | 4
B30103202700 |  | Insulation, rigid, roof deck, extruded polystyrene, 40 PSI compressive strength, 4" thick, R20 | 47700 |  | 0.28 | 197478 | 4
B30104201400 |  | Roof edges, aluminum, duranodic, .050" thick, 6" face | 441 |  | 0.02 | 13119.75 | 4
B30104300040 |  | Flashing, aluminum, no backing sides, .019" | 441 |  | 0.01 | 4043.97 | 4
C |  | Interiors |  | 18.04 | 21.38 | 15295404.7538 | 1
C1010 |  | Partitions |  |  | 2.48 | 1777215.6 | 3
C10101029010 |  | CMU partition, regular weight, hollow, 8" thick, 5/8" gyp board, 1 side, foamed in insulation | 19080 |  | 0.37 | 263304 | 4
C10101266225 |  | Metal partition, 5/8"fire rated gypsum board face, 5/8"fire rated gypsum board base, 3-5/8" @ 24", same opposite face, sound attenuation insulation | 171720 |  | 1.76 | 1260424.8 | 4
C10107109000 |  | 1/2" fire rated gypsum board, taped & finished, painted on metal furring, low VOC paint | 52920 |  | 0.35 | 253486.8 | 4
C1020 |  | Interior Doors |  |  | 3.52 | 2518560 | 3
C10201029010 |  | Door, single leaf, kd steel frame, hollow metal, commercial quality, flush, 3'-0" x 7'-0" x 1-3/8", low VOC paint | 1788.75 |  | 3.52 | 2518560 | 4
C1030 |  | Fittings |  |  | 1.16 | 830200.1538 | 3
C10301100460 |  | Toilet partitions, cubicles, ceiling hung, stainless steel | 330.23 |  | 1.16 | 830200.1538 | 4
C2010 |  | Stair Construction |  |  | 0.85 | 604625 | 3
C20101100760 |  | Stairs, steel, pan tread for conc in-fill, picket rail,20 risers w/ landing | 35 |  | 0.85 | 604625 | 4
C3010 |  | Wall Finishes |  |  | 0.9 | 641088 | 3
C30102301800 |  | Vinyl wall covering, fabric back, medium weight | 228960 |  | 0.74 | 526608 | 4
C30102309000 |  | Painting, interior on plaster and drywall, walls & ceilings, roller work, primer & 2 coats, low VOC | 152640 |  | 0.16 | 114480 | 4
C3020 |  | Floor Finishes |  |  | 5.01 | 3586086 | 3
C30204100080 |  | Carpet tile, nylon, fusion bonded, 18" x 18" or 24" x 24", 35 oz | 429300 |  | 3.24 | 2318220 | 4
C30204101720 |  | Tile, ceramic natural clay | 71550 |  | 0.75 | 533763 | 4
C30204109200 |  | Vinyl, composition tile, 12" x 12" x 1/8" thick, recycled content | 214650 |  | 1.03 | 734103 | 4
C3030 |  | Ceiling Finishes |  |  | 7.46 | 5337630 | 3
C30302107400 |  | Acoustic ceilings, 3/4"mineral fiber, 12" x 12" tile, concealed 2" bar & channel grid, suspended support | 715500 |  | 7.46 | 5337630 | 4
D |  | Services |  | 44.25 | 52.44 | 37520406.0962 | 1
D1010 |  | Elevators and Lifts |  |  | 7.59 | 5432296.1538 | 3
D10101109500 |  | Traction, geared passenger, 3500 lb,15 floors, 10' story height, 2 car group, 350 FPM | 11.01 |  | 7.59 | 5432296.1538 | 4
D2010 |  | Plumbing Fixtures |  |  | 6.09 | 4357620.6577 | 3
D20101109000 |  | Water closet, vitreous china, bowl only w/ auto flush sensor flush valve, wall hung, 1.28 gpf | 673.67 |  | 3.86 | 2762050.1538 | 4
D20102109000 |  | Urinal, vitreous china, wall hung, waterless, ADA | 149.7 |  | 0.15 | 110032.8923 | 4
D20103109000 |  | Lavatory w/trim, vanity top, PE on CI, 20" x 18", faucet w/ hydroelectric powered motion sensor | 299.41 |  | 1.11 | 796428.5538 | 4
D20104404340 |  | Service sink w/trim, PE on CI,wall hung w/rim guard, 24" x 20" | 74.85 |  | 0.6 | 430400.7692 | 4
D20108109000 |  | Drinking fountain, dual bubbler, wall mounted, non recessed, fiberglass, 12" back | 46.78 |  | 0.28 | 197656.875 | 4
D20108209040 |  | Water cooler, electric, wall hung, wheelchair type, 7.5 GPH, GreenSpec certified, ADA | 28.07 |  | 0.09 | 61051.4135 | 4
D2020 |  | Domestic Water Distribution |  |  | 0.2 | 140898.4615 | 3
D20202512260 |  | Gas fired tankless water heater, 3.2 GPM | 44.03 |  | 0.2 | 140898.4615 | 4
D2040 |  | Rain Water Drainage |  |  | 0.21 | 147544.3558 | 3
D20402104200 |  | Roof drain, CI, soil,single hub, 4" diam, 10' high | 13.76 |  | 0.05 | 33573.4615 | 4
D20402104320 |  | Roof drain, CI, soil,single hub, 5" diam, for each additional foot add | 2072.2 |  | 0.16 | 113970.8942 | 4
D3040 |  | Distribution Systems |  |  | 1.73 | 1237333.4135 | 3
D30406301080 |  | Heat recovery pkgs, air to air, enthalpy recovery wheel, 25,000 max CFM | 30.27 |  | 1.73 | 1237333.4135 | 4
D3050 |  | Terminal & Package Units |  |  | 14.9 | 10660950 | 3
D30501573680 |  | Rooftop, multizone, air conditioner, medical centers, 25,000 SF, 58.33 ton SEER 14 | 715500 |  | 14.9 | 10660950 | 4
D4010 |  | Sprinklers |  |  | 2.74 | 1958480.3596 | 3
D40104100620 |  | Wet pipe sprinkler systems, steel, light hazard, 1 floor, 10,000 SF | 42930 |  | 0.21 | 150255 | 4
D40104100740 |  | Wet pipe sprinkler systems, steel, light hazard, each additional floor, 10,000 SF | 672570 |  | 2.43 | 1735230.6 | 4
D40104108950 |  | Standard High Rise Accessory Package 16 story | 2.75 |  | 0.1 | 72994.7596 | 4
D4020 |  | Standpipes |  |  | 0.57 | 409887.5769 | 3
D40203101580 |  | Wet standpipe risers, class III, steel, black, sch 40, 6" diam pipe, 1 floor | 6.6 |  | 0.17 | 118387.7308 | 4
D40203101600 |  | Wet standpipe risers, class III, steel, black, sch 40, 6" diam pipe, additional floors | 52.84 |  | 0.34 | 243049.8462 | 4
D40204103650 |  | Fire pump, electric, with controller, 5" pump, 100 HP, 1000 GPM | 1 |  | 0.06 | 43350 | 4
D40204103700 |  | Fire pump, electric, for jockey pump system, add | 1 |  | 0.01 | 5100 | 4
D5010 |  | Electrical Service/Distribution |  |  | 0.29 | 204948.25 | 3
D50101200520 |  | Overhead service installation, includes breakers, metering, 20' conduit & wire, 3 phase, 4 wire, 120/208 V, 1600 A | 1.47 |  | 0.07 | 48216 | 4
D50102300200 |  | Feeder installation 600 V, including RGS conduit and XHHW wire, 60 A | 100 |  | 0 | 1820 | 4
D50102300240 |  | Feeder installation 600 V, including RGS conduit and XHHW wire, 100 A | 100 |  | 0 | 2770 | 4
D50102300520 |  | Feeder installation 600 V, including RGS conduit and XHHW wire, 1600 A | 234 |  | 0.14 | 98982 | 4
D50102400360 |  | Switchgear installation, incl switchboard, panels & circuit breaker, 120/208 V, 3 phase, 1600 A | 1.43 |  | 0.07 | 53160.25 | 4
D5020 |  | Lighting and Branch Wiring |  |  | 15.41 | 11023707.25 | 3
D50201100640 |  | Receptacles incl plate, box, conduit, wire, 16.5 per 1000 SF, 2.0 W per SF, with transformer | 715500 |  | 4.85 | 3470175 | 4
D50201350320 |  | Miscellaneous power, 1.2 watts | 715500 |  | 0.35 | 250425 | 4
D50201400240 |  | Central air conditioning power, 3 watts | 715500 |  | 0.64 | 457920 | 4
D50201452080 |  | Motor installation, three phase, 460 V, 15 HP motor size | 4 |  | 0.01 | 9560 | 4
D50201550440 |  | Motor feeder systems, three phase, feed to 200 V 5 HP, 230 V 7.5 HP, 460 V 15 HP, 575 V 20 HP | 200 |  | 0 | 2290 | 4
D50201700320 |  | Motor connections, three phase, 200/230/460/575 V, up to 5 HP | 1 |  | 0 | 121 | 4
D50201700560 |  | Motor connections, three phase, 200/230/460/575 V, up to 100 HP | 1 |  | 0 | 549 | 4
D50202601280 |  | LED fixtures, type C, 10 fixtures per 1000 SF | 822825 |  | 6.93 | 4961634.75 | 4
D50202901000 |  | Daylight dimming control system, 10 fixtures per 1000 SF | 357750 |  | 1.48 | 1062517.5 | 4
D50202951000 |  | Lighting on/off control system, 10 fixtures per 1000 SF | 715500 |  | 1.13 | 808515 | 4
D5030 |  | Communications and Security |  |  | 2.29 | 1640008.5577 | 3
D50303101010 |  | Telephone wiring for offices & laboratories, 8 jacks/MSF (cost per MSF) | 1 |  | 0 | 0 | 4
D50309100440 |  | Communication and alarm systems, fire detection, non-addressable, 100 detectors, includes outlets, boxes, conduit and wire | 2.75 |  | 0.26 | 184654.0385 | 4
D50309100456 |  | Communication and alarm systems, fire detection, addressable, 100 detectors, includes outlets, boxes, conduit and wire | 17.89 |  | 1.93 | 1380915 | 4
D50309100462 |  | Fire alarm command center, addressable with voice, excl. wire & conduit | 5.5 |  | 0.1 | 74439.5192 | 4
D50309200110 |  | Internet wiring, 8 data/voice outlets per 1000 S.F. | 1 |  | 0 | 0 | 4
D5090 |  | Other Electrical Systems |  |  | 0.43 | 306731.0596 | 3
D50902100840 |  | Generator sets, w/battery, charger, muffler and transfer switch, diesel engine with fuel tank, 200 kW | 550.38 |  | 0.27 | 193460.1923 | 4
D50902200300 |  | Uninterruptible power supply with standard battery pack, 15 kVA/12.75 kW | 137.6 |  | 0 | 167.8673 | 4
D50904801230 |  | Energy monitoring systems, electrical, three phase, 25 meters | 1 |  | 0.09 | 66500 | 4
D50904802240 |  | Energy monitoring systems, mechanical, BTU, 3 meters w/3 duct & 30 space sensors | 1 |  | 0.05 | 32350 | 4
D50904809000 |  | Energy monitoring systems, Front end display | 16 |  | 0.01 | 10528 | 4
D50904809100 |  | Energy monitoring systems, Computer workstation | 1 |  | 0.01 | 3725 | 4
E |  | Equipment & Furnishings |  | 0.01 | 0.02 | 11551.4723 | 1
E1090 |  | Other Equipment |  |  | 0.01 | 8338.3269 | 3
E10902100180 |  | Waste handling, recycling, tilt truck, plastic, with wheels, 1.0 C.Y., 1000 lb capacity | 2.75 |  | 0.01 | 8338.3269 | 4
E2020 |  | Moveable Furnishings |  |  | 0 | 3213.1454 | 3
E20202300100 |  | Signage, exterior, surface mounted, 24 ga aluminum, 10" x 7", no smoking | 77.05 |  | 0 | 3213.1454 | 4
F |  | Special Construction |  | 0 | 0 | 0 | 1
G |  | Building Sitework |  | 0 | 0 | 0 | 1
SubTotal |  |  |  | 100% | $118.51 | $84,793,119.92
Contractor Fees (General Conditions,Overhead,Profit) |  |  |  | 25.0% | $29.63 | $21,198,279.98
Architectural Fees |  |  |  | 6.0% | $8.89 | $6,359,483.99
User Fees |  |  |  | 0.0% | $0.00 | $0.00
Total Building Cost |  |  |  |  | $157.02 | $112,350,883.89
Audit Trail Notes
Date Time | Description |  |  | User Name |  | Action