## Squarefoot_Estimate
|  | Square Foot Cost Estimate Report |  |  | Date: | 10/31/2022
Estimate Name: |  | office
Building Type: |  | Office, 11-20 Story (Green) with Curtain Wall / Rigid Steel
Location: |  | NATIONAL AVERAGE
Story Count: |  | 17
Story Height (L.F.): |  | 10.00
Floor Area (S.F.): |  | 102000
Labor Type: |  | OPN
Basement Included: |  | No | [5 empty] | Assembly Customization Type:
Data Release: |  | Year 2022 | Costs are derived from a building model with basic components. | [5 empty] | Added
Cost Per Square Foot: |  | $188.71 | Scope differences and market conditions can cause costs to vary significantly. | [5 empty] | Partially Swapped
Building Cost: |  | $19,248,899.66 | [6 empty] | Fully Swapped
|  |  | Quantity | % of Total | Cost Per S.F. | Cost
A |  | Substructure |  | 3.75 | 5.34 | 545101.2077 | 1
A1010 |  | Standard Foundations |  |  | 0.8 | 81168.4615 | 3
A10102506350 |  | Pile caps, 12 piles, 11' - 6" x 8' - 6" x 49", 40 ton capacity, 19" column size, 900 K column | 7.85 |  | 0.38 | 38642.3077 | 4
A10102506600 |  | Pile caps, 14 piles, 11' - 6" x 10' - 9" x 55", 80 ton capacity, 29"column size, 2155 K column | 6.28 |  | 0.42 | 42526.1538 | 4
A1020 |  | Special Foundations |  |  | 3.82 | 390088.3462 | 3
A10201402420 |  | Steel H piles, 50' long, 800K load, end bearing, 12 pile cluster | 7.85 |  | 1.92 | 195565.3846 | 4
A10201402500 |  | Steel H piles, 50' long, 1600K load, end bearing, 10 pile cluster | 6.28 |  | 1.57 | 160218.4615 | 4
A10202104620 |  | Grade beam, 30' span, 52" deep, 14" wide, 12 KLF load | 157 |  | 0.34 | 34304.5 | 4
A1030 |  | Slab on Grade |  |  | 0.35 | 35940 | 3
A10301209000 |  | Slab on grade, 4" thick, non industrial, reinforced, recycled plastic vapor barrier | 6000 |  | 0.35 | 35940 | 4
A2010 |  | Basement Excavation |  |  | 0.02 | 1920 | 3
A20101104560 |  | Excavate and fill, 10,000 SF, 4' deep, sand, gravel, or common earth, on site storage | 6000 |  | 0.02 | 1920 | 4
A2020 |  | Basement Walls |  |  | 0.35 | 35984.4 | 3
A20201111560 |  | Foundation wall, CIP, 4' wall height, direct chute, .148 CY/LF, 7.2 PLF, 12" thick, 3" XPS R15 | 376.8 |  | 0.35 | 35984.4 | 4
B |  | Shell |  | 38.15 | 54.33 | 5541865.9514 | 1
B1010 |  | Floor Construction |  |  | 30.03 | 3062665.0745 | 3
B10102081600 |  | Steel column, W5, 50 K, 10' unsupported length, 16 PLF | 62.77 |  | 0.03 | 2849.7231 | 4
B10102084800 |  | Steel column, W10, 200 KIPS, 16' unsupported height, 49 PLF | 172.62 |  | 0.18 | 18435.3231 | 4
B10102085400 |  | Steel column, W12, 300 KIPS, 16' unsupported height, 72 PLF | 138.09 |  | 0.21 | 21100.5046 | 4
B10102086000 |  | Steel column, W12, 400 KIPS, 16' unsupported height, 87 PLF | 172.62 |  | 0.31 | 31554.0923 | 4
B10102086600 |  | Steel column, TS14, 500 KIPS, 16' unsupported height, 109 PLF | 172.62 |  | 0.39 | 39321.7846 | 4
B10102087800 |  | Steel column, W14, 700 KIPS, 16' unsupported height, 145 PLF | 172.62 |  | 0.51 | 51750.0923 | 4
B10102088300 |  | Steel column, W14, 800 KIPS, 16' unsupported height, 159 PLF | 172.62 |  | 0.55 | 56583.3231 | 4
B10102089200 |  | Steel column, W14, 1000 KIPS, 16' unsupported height, 193 PLF | 427.62 |  | 1.67 | 170105.4 | 4
B10102524300 |  | Floor, composite concrete slab on fireproofed W beam, 4.5" slab, 25'x25' bay, 20.5" total depth, 75 PSF superimposed load, 136 PSF total | 96000 |  | 26.02 | 2654400 | 4
B10107203900 |  | Fireproofing, sprayed fiber, 1.5" thick, 8" steel column, 2 hour rating, 6.3 PLF | 1197.32 |  | 0.13 | 13218.4468 | 4
B10107204050 |  | Fireproofing, sprayed fiber, 1.5" thick, 10" steel column, 2 hour rating, 7.9 PLF | 172.62 |  | 0.02 | 2304.4154 | 4
B10107204200 |  | Fireproofing, sprayed fiber, 1.5" thick, 14" steel column, 2 hour rating,10.8 PLF | 62.77 |  | 0.01 | 1041.9692 | 4
B1020 |  | Roof Construction |  |  | 0.57 | 58320 | 3
B10201123300 |  | Roof, steel joists, beams, 1.5" 22 ga metal deck, on columns, 25'x25' bay, 20" deep, 40 PSF superimposed load, 60 PSF total load | 6000 |  | 0.57 | 58320 | 4
B2020 |  | Exterior Windows |  |  | 22.44 | 2288507.36 | 3
B20202102000 |  | Aluminum flush tube frame, thermo-break frame, 2.25" x 4.5", 5'x6' opening, no intermediate horizontals | 26690 |  | 7.68 | 783351.5 | 4
B20202201700 |  | Glazing panel, insulating, 1" thick units, 2 lites, light and heat reflective glass, tinted | 26690 |  | 14.59 | 1487967.5 | 4
B20202209000 |  | Curtain wall insulation and finishing, 3" R15 rigid insulation, metal furring 24" oc, gypsum board 5/8" thick | 2669 |  | 0.17 | 17188.36 | 4
B2030 |  | Exterior Doors |  |  | 0.87 | 88583.0769 | 3
B20301106550 |  | Door, aluminum & glass, without transom, full vision, double door, hardware, 6'-0" x 7'-0" opening | 6.28 |  | 0.46 | 46920 | 4
B20301107250 |  | Door, aluminum & glass, with transom, non-standard, double door, hardware, 6'-0" x 10'-0" opening | 4.71 |  | 0.41 | 41663.0769 | 4
B3010 |  | Roof Coverings |  |  | 0.43 | 43790.44 | 3
B30101206200 |  | Roofing, single ply membrane, reinforced, PVC, 48 mils, fully adhered, adhesive | 6000 |  | 0.13 | 12840 | 4
B30103202700 |  | Insulation, rigid, roof deck, extruded polystyrene, 40 PSI compressive strength, 4" thick, R20 | 6000 |  | 0.24 | 24840 | 4
B30104201400 |  | Roof edges, aluminum, duranodic, .050" thick, 6" face | 157 |  | 0.05 | 4670.75 | 4
B30104300040 |  | Flashing, aluminum, no backing sides, .019" | 157 |  | 0.01 | 1439.69 | 4
C |  | Interiors |  | 19.03 | 27.11 | 2765047.6646 | 1
C1010 |  | Partitions |  |  | 3.13 | 319495.28 | 3
C10101029010 |  | CMU partition, regular weight, hollow, 8" thick, 5/8" gyp board, 1 side, foamed in insulation | 2720 |  | 0.37 | 37536 | 4
C10101266225 |  | Metal partition, 5/8"fire rated gypsum board face, 5/8"fire rated gypsum board base, 3-5/8" @ 24", same opposite face, sound attenuation insulation | 24480 |  | 1.76 | 179683.2 | 4
C10107109000 |  | 1/2" fire rated gypsum board, taped & finished, painted on metal furring, low VOC paint | 21352 |  | 1 | 102276.08 | 4
C1020 |  | Interior Doors |  |  | 3.52 | 359040 | 3
C10201029010 |  | Door, single leaf, kd steel frame, hollow metal, commercial quality, flush, 3'-0" x 7'-0" x 1-3/8", low VOC paint | 255 |  | 3.52 | 359040 | 4
C1030 |  | Fittings |  |  | 1.16 | 118351.3846 | 3
C10301100460 |  | Toilet partitions, cubicles, ceiling hung, stainless steel | 47.08 |  | 1.16 | 118351.3846 | 4
C2010 |  | Stair Construction |  |  | 5.93 | 604625 | 3
C20101100760 |  | Stairs, steel, pan tread for conc in-fill, picket rail,20 risers w/ landing | 35 |  | 5.93 | 604625 | 4
C3010 |  | Wall Finishes |  |  | 0.9 | 91392 | 3
C30102301800 |  | Vinyl wall covering, fabric back, medium weight | 32640 |  | 0.74 | 75072 | 4
C30102309000 |  | Painting, interior on plaster and drywall, walls & ceilings, roller work, primer & 2 coats, low VOC | 21760 |  | 0.16 | 16320 | 4
C3020 |  | Floor Finishes |  |  | 5.01 | 511224 | 3
C30204100080 |  | Carpet tile, nylon, fusion bonded, 18" x 18" or 24" x 24", 35 oz | 61200 |  | 3.24 | 330480 | 4
C30204101720 |  | Tile, ceramic natural clay | 10200 |  | 0.75 | 76092 | 4
C30204109200 |  | Vinyl, composition tile, 12" x 12" x 1/8" thick, recycled content | 30600 |  | 1.03 | 104652 | 4
C3030 |  | Ceiling Finishes |  |  | 7.46 | 760920 | 3
C30302107400 |  | Acoustic ceilings, 3/4"mineral fiber, 12" x 12" tile, concealed 2" bar & channel grid, suspended support | 102000 |  | 7.46 | 760920 | 4
D |  | Services |  | 39.06 | 55.63 | 5673809.8654 | 1
D1010 |  | Elevators and Lifts |  |  | 7.59 | 774415.3846 | 3
D10101109500 |  | Traction, geared passenger, 3500 lb,15 floors, 10' story height, 2 car group, 350 FPM | 1.57 |  | 7.59 | 774415.3846 | 4
D2010 |  | Plumbing Fixtures |  |  | 6.09 | 621212.1692 | 3
D20101109000 |  | Water closet, vitreous china, bowl only w/ auto flush sensor flush valve, wall hung, 1.28 gpf | 96.04 |  | 3.86 | 393751.3846 | 4
D20102109000 |  | Urinal, vitreous china, wall hung, waterless, ADA | 21.34 |  | 0.15 | 15686.0308 | 4
D20103109000 |  | Lavatory w/trim, vanity top, PE on CI, 20" x 18", faucet w/ hydroelectric powered motion sensor | 42.68 |  | 1.11 | 113536.9846 | 4
D20104404340 |  | Service sink w/trim, PE on CI,wall hung w/rim guard, 24" x 20" | 10.67 |  | 0.6 | 61356.9231 | 4
D20108109000 |  | Drinking fountain, dual bubbler, wall mounted, non recessed, fiberglass, 12" back | 6.67 |  | 0.28 | 28177.5 | 4
D20108209040 |  | Water cooler, electric, wall hung, wheelchair type, 7.5 GPH, GreenSpec certified, ADA | 4 |  | 0.09 | 8703.3462 | 4
D2020 |  | Domestic Water Distribution |  |  | 0.2 | 20086.1538 | 3
D20202512260 |  | Gas fired tankless water heater, 3.2 GPM | 6.28 |  | 0.2 | 20086.1538 | 4
D2040 |  | Rain Water Drainage |  |  | 0.21 | 21033.5769 | 3
D20402104200 |  | Roof drain, CI, soil,single hub, 4" diam, 10' high | 1.96 |  | 0.05 | 4786.1538 | 4
D20402104320 |  | Roof drain, CI, soil,single hub, 5" diam, for each additional foot add | 295.41 |  | 0.16 | 16247.4231 | 4
D3040 |  | Distribution Systems |  |  | 1.73 | 176391.3462 | 3
D30406301080 |  | Heat recovery pkgs, air to air, enthalpy recovery wheel, 25,000 max CFM | 4.32 |  | 1.73 | 176391.3462 | 4
D3050 |  | Terminal & Package Units |  |  | 14.9 | 1519800 | 3
D30501573680 |  | Rooftop, multizone, air conditioner, medical centers, 25,000 SF, 58.33 ton SEER 14 | 102000 |  | 14.9 | 1519800 | 4
D4010 |  | Sprinklers |  |  | 2.74 | 279196.3615 | 3
D40104100620 |  | Wet pipe sprinkler systems, steel, light hazard, 1 floor, 10,000 SF | 6120 |  | 0.21 | 21420 | 4
D40104100740 |  | Wet pipe sprinkler systems, steel, light hazard, each additional floor, 10,000 SF | 95880 |  | 2.43 | 247370.4 | 4
D40104108950 |  | Standard High Rise Accessory Package 16 story | 0.39 |  | 0.1 | 10405.9615 | 4
D4020 |  | Standpipes |  |  | 0.98 | 99975.6923 | 3
D40203101580 |  | Wet standpipe risers, class III, steel, black, sch 40, 6" diam pipe, 1 floor | 0.94 |  | 0.17 | 16877.0769 | 4
D40203101600 |  | Wet standpipe risers, class III, steel, black, sch 40, 6" diam pipe, additional floors | 7.53 |  | 0.34 | 34648.6154 | 4
D40204103650 |  | Fire pump, electric, with controller, 5" pump, 100 HP, 1000 GPM | 1 |  | 0.42 | 43350 | 4
D40204103700 |  | Fire pump, electric, for jockey pump system, add | 1 |  | 0.05 | 5100 | 4
D5010 |  | Electrical Service/Distribution |  |  | 2.01 | 204948.25 | 3
D50101200520 |  | Overhead service installation, includes breakers, metering, 20' conduit & wire, 3 phase, 4 wire, 120/208 V, 1600 A | 1.47 |  | 0.47 | 48216 | 4
D50102300200 |  | Feeder installation 600 V, including RGS conduit and XHHW wire, 60 A | 100 |  | 0.02 | 1820 | 4
D50102300240 |  | Feeder installation 600 V, including RGS conduit and XHHW wire, 100 A | 100 |  | 0.03 | 2770 | 4
D50102300520 |  | Feeder installation 600 V, including RGS conduit and XHHW wire, 1600 A | 234 |  | 0.97 | 98982 | 4
D50102400360 |  | Switchgear installation, incl switchboard, panels & circuit breaker, 120/208 V, 3 phase, 1600 A | 1.43 |  | 0.52 | 53160.25 | 4
D5020 |  | Lighting and Branch Wiring |  |  | 15.51 | 1582249 | 3
D50201100640 |  | Receptacles incl plate, box, conduit, wire, 16.5 per 1000 SF, 2.0 W per SF, with transformer | 102000 |  | 4.85 | 494700 | 4
D50201350320 |  | Miscellaneous power, 1.2 watts | 102000 |  | 0.35 | 35700 | 4
D50201400240 |  | Central air conditioning power, 3 watts | 102000 |  | 0.64 | 65280 | 4
D50201452080 |  | Motor installation, three phase, 460 V, 15 HP motor size | 4 |  | 0.09 | 9560 | 4
D50201550440 |  | Motor feeder systems, three phase, feed to 200 V 5 HP, 230 V 7.5 HP, 460 V 15 HP, 575 V 20 HP | 200 |  | 0.02 | 2290 | 4
D50201700320 |  | Motor connections, three phase, 200/230/460/575 V, up to 5 HP | 1 |  | 0 | 121 | 4
D50201700560 |  | Motor connections, three phase, 200/230/460/575 V, up to 100 HP | 1 |  | 0.01 | 549 | 4
D50202601280 |  | LED fixtures, type C, 10 fixtures per 1000 SF | 117300 |  | 6.93 | 707319 | 4
D50202901000 |  | Daylight dimming control system, 10 fixtures per 1000 SF | 51000 |  | 1.48 | 151470 | 4
D50202951000 |  | Lighting on/off control system, 10 fixtures per 1000 SF | 102000 |  | 1.13 | 115260 | 4
D5030 |  | Communications and Security |  |  | 2.29 | 233795.7692 | 3
D50303101010 |  | Telephone wiring for offices & laboratories, 8 jacks/MSF (cost per MSF) | 1 |  | 0 | 0 | 4
D50309100440 |  | Communication and alarm systems, fire detection, non-addressable, 100 detectors, includes outlets, boxes, conduit and wire | 0.39 |  | 0.26 | 26323.8462 | 4
D50309100456 |  | Communication and alarm systems, fire detection, addressable, 100 detectors, includes outlets, boxes, conduit and wire | 2.55 |  | 1.93 | 196860 | 4
D50309100462 |  | Fire alarm command center, addressable with voice, excl. wire & conduit | 0.78 |  | 0.1 | 10611.9231 | 4
D50309200110 |  | Internet wiring, 8 data/voice outlets per 1000 S.F. | 1 |  | 0 | 0 | 4
D5090 |  | Other Electrical Systems |  |  | 1.38 | 140706.1615 | 3
D50902100840 |  | Generator sets, w/battery, charger, muffler and transfer switch, diesel engine with fuel tank, 200 kW | 78.46 |  | 0.27 | 27579.2308 | 4
D50902200300 |  | Uninterruptible power supply with standard battery pack, 15 kVA/12.75 kW | 19.62 |  | 0 | 23.9308 | 4
D50904801230 |  | Energy monitoring systems, electrical, three phase, 25 meters | 1 |  | 0.65 | 66500 | 4
D50904802240 |  | Energy monitoring systems, mechanical, BTU, 3 meters w/3 duct & 30 space sensors | 1 |  | 0.32 | 32350 | 4
D50904809000 |  | Energy monitoring systems, Front end display | 16 |  | 0.1 | 10528 | 4
D50904809100 |  | Energy monitoring systems, Computer workstation | 1 |  | 0.04 | 3725 | 4
E |  | Equipment & Furnishings |  | 0.01 | 0.02 | 1646.7508 | 1
E1090 |  | Other Equipment |  |  | 0.01 | 1188.6923 | 3
E10902100180 |  | Waste handling, recycling, tilt truck, plastic, with wheels, 1.0 C.Y., 1000 lb capacity | 0.39 |  | 0.01 | 1188.6923 | 4
E2020 |  | Moveable Furnishings |  |  | 0 | 458.0585 | 3
E20202300100 |  | Signage, exterior, surface mounted, 24 ga aluminum, 10" x 7", no smoking | 10.98 |  | 0 | 458.0585 | 4
F |  | Special Construction |  | 0 | 0 | 0 | 1
G |  | Building Sitework |  | 0 | 0 | 0 | 1
SubTotal |  |  |  | 100% | $142.43 | $14,527,471.44
Contractor Fees (General Conditions,Overhead,Profit) |  |  |  | 25.0% | $35.61 | $3,631,867.86
Architectural Fees |  |  |  | 6.0% | $10.68 | $1,089,560.36
User Fees |  |  |  | 0.0% | $0.00 | $0.00
Total Building Cost |  |  |  |  | $188.71 | $19,248,899.66
Audit Trail Notes
Date Time | Description |  |  | User Name |  | Action